## Heating_models
Heating model for bare steel and protected members
Steel profile
Section factor, Am/V | 137.278 | m-1
Specific mass, rs | 7850 | kg/m³
Relative emissivity, e | 0.5 | -
Convection coefficient, ac | 25 | W/m²K
Protection
Section factor, Ap/V | 137.278 | m-1
Specific mass, rp | 300 | kg/m³
Specific heat, cp | 1850 | J/kgK
Thermal conductivity, lp | 0.2 | W/mK
Thickness, dp | 0.012 | m
[5 empty] | Bare steel |  |  | Protected member
|  |  | Time (min.) | q ISO | q steel | cpa(q) | phi | dT | q steel | cpa(q)
|  |  | 0 | 20 | 20 | 439.8018 | 0.26482 | 0 | 20 | 439.8018
|  |  | 0.083333 | 96.5378 | 20.444 | 440.1158 | 0.26482 | -1.8209 | 20 | 439.8018
|  |  | 0.16667 | 146.952 | 21.2057 | 440.6532 | 0.26482 | -0.96636 | 20 | 439.8018
|  |  | 0.25 | 184.6068 | 22.2209 | 441.3666 | 0.26482 | -0.5093 | 20 | 439.8018
|  |  | 0.33333 | 214.6736 | 23.449 | 442.2255 | 0.26482 | -0.21412 | 20 | 439.8018
|  |  | 0.41667 | 239.7036 | 24.862 | 443.2078 | 0.26482 | -0.0027469 | 20 | 439.8018
|  |  | 0.5 | 261.1447 | 26.4387 | 444.2968 | 0.26482 | 0.15885 | 20.1588 | 439.9142
|  |  | 0.58333 | 279.898 | 28.1622 | 445.4786 | 0.26475 | 0.28753 | 20.4464 | 440.1175
|  |  | 0.66667 | 296.5632 | 30.0191 | 446.7419 | 0.26463 | 0.39327 | 20.8396 | 440.3952
|  |  | 0.75 | 311.5588 | 31.9978 | 448.0767 | 0.26446 | 0.48221 | 21.3219 | 440.735
|  |  | 0.83333 | 325.1893 | 34.0886 | 449.4746 | 0.26426 | 0.55841 | 21.8803 | 441.1276
|  |  | 0.91667 | 337.6825 | 36.2831 | 450.928 | 0.26402 | 0.62465 | 22.5049 | 441.5657
|  |  | 1 | 349.2137 | 38.5737 | 452.4303 | 0.26376 | 0.68291 | 23.1878 | 442.0432
|  |  | 1.0833 | 359.9205 | 40.9539 | 453.9754 | 0.26348 | 0.73465 | 23.9225 | 442.5553
|  |  | 1.1667 | 369.913 | 43.4178 | 455.5578 | 0.26317 | 0.78097 | 24.7034 | 443.0979
|  |  | 1.25 | 379.2805 | 45.9599 | 457.1727 | 0.26285 | 0.82273 | 25.5262 | 443.6675
|  |  | 1.3333 | 388.0966 | 48.5754 | 458.8155 | 0.26251 | 0.8606 | 26.3868 | 444.2611
|  |  | 1.4167 | 396.4228 | 51.2598 | 460.4823 | 0.26216 | 0.89511 | 27.2819 | 444.8761
|  |  | 1.5 | 404.3105 | 54.0092 | 462.1691 | 0.2618 | 0.9267 | 28.2086 | 445.5103
|  |  | 1.5833 | 411.8036 | 56.8197 | 463.8727 | 0.26143 | 0.95572 | 29.1643 | 446.1616
|  |  | 1.6667 | 418.9398 | 59.6879 | 465.5899 | 0.26104 | 0.98248 | 30.1468 | 446.8284
|  |  | 1.75 | 425.7515 | 62.6106 | 467.3179 | 0.26065 | 1.0072 | 31.154 | 447.5089
|  |  | 1.8333 | 432.2669 | 65.5848 | 469.054 | 0.26026 | 1.0301 | 32.1842 | 448.2018
|  |  | 1.9167 | 438.5108 | 68.6077 | 470.7958 | 0.25986 | 1.0515 | 33.2356 | 448.9058
|  |  | 2 | 444.5049 | 71.6768 | 472.5412 | 0.25945 | 1.0713 | 34.3069 | 449.6198
|  |  | 2.0833 | 450.2683 | 74.7897 | 474.2881 | 0.25904 | 1.0898 | 35.3967 | 450.3427
|  |  | 2.1667 | 455.8183 | 77.944 | 476.0347 | 0.25862 | 1.1071 | 36.5038 | 451.0735
|  |  | 2.25 | 461.17 | 81.1376 | 477.7794 | 0.2582 | 1.1233 | 37.6271 | 451.8113
|  |  | 2.3333 | 466.3371 | 84.3686 | 479.5206 | 0.25778 | 1.1384 | 38.7655 | 452.5554
|  |  | 2.4167 | 471.332 | 87.6351 | 481.257 | 0.25736 | 1.1527 | 39.9182 | 453.305
|  |  | 2.5 | 476.1657 | 90.9353 | 482.9873 | 0.25693 | 1.166 | 41.0842 | 454.0595
|  |  | 2.5833 | 480.8483 | 94.2674 | 484.7105 | 0.2565 | 1.1786 | 42.2628 | 454.8182
|  |  | 2.6667 | 485.389 | 97.6301 | 486.4255 | 0.25608 | 1.1904 | 43.4532 | 455.5805
|  |  | 2.75 | 489.7961 | 101.0216 | 488.1314 | 0.25565 | 1.2015 | 44.6548 | 456.3459
|  |  | 2.8333 | 494.0773 | 104.4406 | 489.8274 | 0.25522 | 1.212 | 45.8668 | 457.1139
|  |  | 2.9167 | 498.2396 | 107.8858 | 491.5129 | 0.25479 | 1.2219 | 47.0886 | 457.884
|  |  | 3 | 502.2893 | 111.3558 | 493.1873 | 0.25436 | 1.2312 | 48.3198 | 458.6559
|  |  | 3.0833 | 506.2325 | 114.8495 | 494.85 | 0.25393 | 1.24 | 49.5598 | 459.429
|  |  | 3.1667 | 510.0745 | 118.3656 | 496.5006 | 0.25351 | 1.2483 | 50.8081 | 460.2032
|  |  | 3.25 | 513.8205 | 121.9031 | 498.1387 | 0.25308 | 1.2561 | 52.0642 | 460.9779
|  |  | 3.3333 | 517.4751 | 125.4609 | 499.764 | 0.25265 | 1.2635 | 53.3277 | 461.7529
|  |  | 3.4167 | 521.0427 | 129.0379 | 501.3763 | 0.25223 | 1.2705 | 54.5983 | 462.5279
|  |  | 3.5 | 524.5273 | 132.6333 | 502.9755 | 0.25181 | 1.2771 | 55.8754 | 463.3027
|  |  | 3.5833 | 527.9327 | 136.2459 | 504.5614 | 0.25139 | 1.2833 | 57.1587 | 464.0768
|  |  | 3.6667 | 531.2624 | 139.8751 | 506.1339 | 0.25097 | 1.2892 | 58.4479 | 464.8502
|  |  | 3.75 | 534.5198 | 143.5198 | 507.6931 | 0.25055 | 1.2948 | 59.7427 | 465.6226
|  |  | 3.8333 | 537.7078 | 147.1792 | 509.2389 | 0.25013 | 1.3001 | 61.0428 | 466.3937
|  |  | 3.9167 | 540.8294 | 150.8526 | 510.7715 | 0.24972 | 1.305 | 62.3478 | 467.1635
|  |  | 4 | 543.8873 | 154.5391 | 512.2911 | 0.24931 | 1.3097 | 63.6575 | 467.9316
|  |  | 4.0833 | 546.884 | 158.2381 | 513.7977 | 0.2489 | 1.3141 | 64.9716 | 468.6979
|  |  | 4.1667 | 549.822 | 161.9487 | 515.2915 | 0.24849 | 1.3183 | 66.2899 | 469.4623
|  |  | 4.25 | 552.7035 | 165.6703 | 516.7729 | 0.24809 | 1.3222 | 67.6121 | 470.2247
|  |  | 4.3333 | 555.5306 | 169.4023 | 518.242 | 0.24769 | 1.3259 | 68.9381 | 470.9848
|  |  | 4.4167 | 558.3053 | 173.1438 | 519.6992 | 0.24729 | 1.3294 | 70.2675 | 471.7426
|  |  | 4.5 | 561.0296 | 176.8943 | 521.1449 | 0.24689 | 1.3327 | 71.6002 | 472.4979
|  |  | 4.5833 | 563.7052 | 180.6531 | 522.5793 | 0.24649 | 1.3358 | 72.9359 | 473.2506
|  |  | 4.6667 | 566.3339 | 184.4197 | 524.0028 | 0.2461 | 1.3387 | 74.2746 | 474.0007
|  |  | 4.75 | 568.9173 | 188.1935 | 525.4159 | 0.24571 | 1.3414 | 75.616 | 474.7479
|  |  | 4.8333 | 571.4569 | 191.9737 | 526.819 | 0.24533 | 1.3439 | 76.9599 | 475.4923
|  |  | 4.9167 | 573.9541 | 195.76 | 528.2126 | 0.24494 | 1.3463 | 78.3062 | 476.2338
|  |  | 5 | 576.4104 | 199.5516 | 529.597 | 0.24456 | 1.3485 | 79.6547 | 476.9722
|  |  | 5.0833 | 578.8271 | 203.3481 | 530.9728 | 0.24418 | 1.3506 | 81.0053 | 477.7076
|  |  | 5.1667 | 581.2055 | 207.1489 | 532.3404 | 0.24381 | 1.3525 | 82.3578 | 478.4398
|  |  | 5.25 | 583.5466 | 210.9536 | 533.7005 | 0.24343 | 1.3543 | 83.7122 | 479.1688
|  |  | 5.3333 | 585.8518 | 214.7614 | 535.0534 | 0.24306 | 1.356 | 85.0682 | 479.8945
|  |  | 5.4167 | 588.122 | 218.5721 | 536.3998 | 0.24269 | 1.3575 | 86.4257 | 480.6169
|  |  | 5.5 | 590.3583 | 222.385 | 537.7402 | 0.24233 | 1.3589 | 87.7846 | 481.3359
|  |  | 5.5833 | 592.5618 | 226.1996 | 539.0751 | 0.24197 | 1.3602 | 89.1449 | 482.0516
|  |  | 5.6667 | 594.7333 | 230.0155 | 540.4051 | 0.24161 | 1.3614 | 90.5063 | 482.7638
|  |  | 5.75 | 596.8738 | 233.8322 | 541.7308 | 0.24125 | 1.3625 | 91.8688 | 483.4725
|  |  | 5.8333 | 598.9841 | 237.6492 | 543.0527 | 0.2409 | 1.3635 | 93.2323 | 484.1777
|  |  | 5.9167 | 601.0651 | 241.466 | 544.3715 | 0.24055 | 1.3644 | 94.5967 | 484.8795
|  |  | 6 | 603.1176 | 245.2821 | 545.6876 | 0.2402 | 1.3652 | 95.9619 | 485.5776
|  |  | 6.0833 | 605.1424 | 249.0972 | 547.0017 | 0.23985 | 1.3659 | 97.3277 | 486.2722
|  |  | 6.1667 | 607.1402 | 252.9107 | 548.3143 | 0.23951 | 1.3665 | 98.6942 | 486.9632
|  |  | 6.25 | 609.1117 | 256.7222 | 549.6262 | 0.23917 | 1.367 | 100.0612 | 487.6507
|  |  | 6.3333 | 611.0576 | 260.5312 | 550.9377 | 0.23883 | 1.3674 | 101.4286 | 488.3345
|  |  | 6.4167 | 612.9785 | 264.3374 | 552.2496 | 0.2385 | 1.3678 | 102.7964 | 489.0147
|  |  | 6.5 | 614.8752 | 268.1402 | 553.5623 | 0.23817 | 1.3681 | 104.1645 | 489.6913
|  |  | 6.5833 | 616.7481 | 271.9393 | 554.8765 | 0.23784 | 1.3683 | 105.5328 | 490.3643
|  |  | 6.6667 | 618.5979 | 275.7342 | 556.1928 | 0.23751 | 1.3684 | 106.9012 | 491.0336
|  |  | 6.75 | 620.4251 | 279.5244 | 557.5116 | 0.23719 | 1.3685 | 108.2697 | 491.6993
|  |  | 6.8333 | 622.2303 | 283.3096 | 558.8336 | 0.23687 | 1.3685 | 109.6383 | 492.3614
|  |  | 6.9167 | 624.0141 | 287.0894 | 560.1594 | 0.23655 | 1.3685 | 111.0068 | 493.0199
|  |  | 7 | 625.7768 | 290.8633 | 561.4894 | 0.23623 | 1.3684 | 112.3752 | 493.6748
|  |  | 7.0833 | 627.5191 | 294.6309 | 562.8242 | 0.23592 | 1.3682 | 113.7434 | 494.326
|  |  | 7.1667 | 629.2413 | 298.3918 | 564.1644 | 0.23561 | 1.368 | 115.1114 | 494.9737
|  |  | 7.25 | 630.9439 | 302.1457 | 565.5104 | 0.2353 | 1.3677 | 116.4791 | 495.6178
|  |  | 7.3333 | 632.6275 | 305.8921 | 566.8629 | 0.235 | 1.3674 | 117.8465 | 496.2583
|  |  | 7.4167 | 634.2923 | 309.6306 | 568.2221 | 0.23469 | 1.367 | 119.2135 | 496.8952
|  |  | 7.5 | 635.9388 | 313.3608 | 569.5888 | 0.23439 | 1.3666 | 120.5801 | 497.5286
|  |  | 7.5833 | 637.5674 | 317.0825 | 570.9633 | 0.23409 | 1.3661 | 121.9462 | 498.1585
|  |  | 7.6667 | 639.1785 | 320.7951 | 572.3461 | 0.2338 | 1.3656 | 123.3118 | 498.7848
|  |  | 7.75 | 640.7725 | 324.4983 | 573.7377 | 0.2335 | 1.365 | 124.6768 | 499.4077
|  |  | 7.8333 | 642.3497 | 328.1918 | 575.1385 | 0.23321 | 1.3644 | 126.0413 | 500.0271
|  |  | 7.9167 | 643.9104 | 331.8752 | 576.5489 | 0.23292 | 1.3638 | 127.4051 | 500.643
|  |  | 8 | 645.4551 | 335.548 | 577.9693 | 0.23264 | 1.3631 | 128.7682 | 501.2555
|  |  | 8.0833 | 646.984 | 339.2101 | 579.4002 | 0.23235 | 1.3624 | 130.1305 | 501.8646
|  |  | 8.1667 | 648.4975 | 342.8609 | 580.842 | 0.23207 | 1.3616 | 131.4921 | 502.4702
|  |  | 8.25 | 649.9958 | 346.5002 | 582.2949 | 0.23179 | 1.3608 | 132.8529 | 503.0725
|  |  | 8.3333 | 651.4793 | 350.1277 | 583.7593 | 0.23151 | 1.36 | 134.2129 | 503.6715
|  |  | 8.4167 | 652.9482 | 353.7429 | 585.2357 | 0.23124 | 1.3591 | 135.572 | 504.2671
|  |  | 8.5 | 654.4029 | 357.3457 | 586.7242 | 0.23096 | 1.3582 | 136.9303 | 504.8595
|  |  | 8.5833 | 655.8436 | 360.9356 | 588.2253 | 0.23069 | 1.3573 | 138.2876 | 505.4485
|  |  | 8.6667 | 657.2706 | 364.5123 | 589.7391 | 0.23042 | 1.3563 | 139.6439 | 506.0343
|  |  | 8.75 | 658.6841 | 368.0755 | 591.266 | 0.23016 | 1.3553 | 140.9992 | 506.6169
|  |  | 8.8333 | 660.0844 | 371.625 | 592.8062 | 0.22989 | 1.3543 | 142.3536 | 507.1963
|  |  | 8.9167 | 661.4718 | 375.1604 | 594.36 | 0.22963 | 1.3533 | 143.7068 | 507.7726
|  |  | 9 | 662.8464 | 378.6814 | 595.9275 | 0.22937 | 1.3522 | 145.059 | 508.3457
|  |  | 9.0833 | 664.2085 | 382.1878 | 597.5091 | 0.22911 | 1.3511 | 146.4102 | 508.9157
|  |  | 9.1667 | 665.5583 | 385.6792 | 599.1048 | 0.22885 | 1.35 | 147.7601 | 509.4826
|  |  | 9.25 | 666.8961 | 389.1555 | 600.7148 | 0.2286 | 1.3488 | 149.109 | 510.0464
|  |  | 9.3333 | 668.2221 | 392.6163 | 602.3393 | 0.22835 | 1.3477 | 150.4567 | 510.6073
|  |  | 9.4167 | 669.5364 | 396.0614 | 603.9784 | 0.2281 | 1.3465 | 151.8031 | 511.1651
|  |  | 9.5 | 670.8393 | 399.4905 | 605.6323 | 0.22785 | 1.3453 | 153.1484 | 511.72
|  |  | 9.5833 | 672.131 | 402.9034 | 607.3011 | 0.2276 | 1.344 | 154.4924 | 512.2719
|  |  | 9.6667 | 673.4116 | 406.2999 | 608.9847 | 0.22736 | 1.3428 | 155.8352 | 512.821
|  |  | 9.75 | 674.6813 | 409.6797 | 610.6834 | 0.22711 | 1.3415 | 157.1767 | 513.3672
|  |  | 9.8333 | 675.9404 | 413.0426 | 612.3972 | 0.22687 | 1.3402 | 158.5169 | 513.9105
|  |  | 9.9167 | 677.189 | 416.3884 | 614.126 | 0.22663 | 1.3389 | 159.8558 | 514.451
|  |  | 10 | 678.4273 | 419.717 | 615.8699 | 0.22639 | 1.3375 | 161.1933 | 514.9888
|  |  | 10.0833 | 679.6555 | 423.028 | 617.629 | 0.22616 | 1.3362 | 162.5295 | 515.5238
|  |  | 10.1667 | 680.8736 | 426.3213 | 619.4032 | 0.22592 | 1.3348 | 163.8643 | 516.0561
|  |  | 10.25 | 682.0819 | 429.5967 | 621.1925 | 0.22569 | 1.3334 | 165.1978 | 516.5857
|  |  | 10.3333 | 683.2806 | 432.8541 | 622.9969 | 0.22546 | 1.332 | 166.5298 | 517.1126
|  |  | 10.4167 | 684.4697 | 436.0933 | 624.8162 | 0.22523 | 1.3306 | 167.8604 | 517.637
|  |  | 10.5 | 685.6495 | 439.3141 | 626.6505 | 0.225 | 1.3292 | 169.1896 | 518.1587
|  |  | 10.5833 | 686.8201 | 442.5164 | 628.4997 | 0.22477 | 1.3277 | 170.5174 | 518.6779
|  |  | 10.6667 | 687.9816 | 445.7 | 630.3637 | 0.22455 | 1.3263 | 171.8436 | 519.1946
|  |  | 10.75 | 689.1341 | 448.8648 | 632.2423 | 0.22432 | 1.3248 | 173.1684 | 519.7088
|  |  | 10.8333 | 690.2779 | 452.0106 | 634.1355 | 0.2241 | 1.3233 | 174.4917 | 520.2205
|  |  | 10.9167 | 691.413 | 455.1374 | 636.0431 | 0.22388 | 1.3218 | 175.8135 | 520.7298
|  |  | 11 | 692.5396 | 458.2451 | 637.965 | 0.22366 | 1.3203 | 177.1338 | 521.2367
|  |  | 11.0833 | 693.6577 | 461.3334 | 639.901 | 0.22344 | 1.3188 | 178.4526 | 521.7412
|  |  | 11.1667 | 694.7676 | 464.4024 | 641.8511 | 0.22323 | 1.3172 | 179.7698 | 522.2434
|  |  | 11.25 | 695.8693 | 467.452 | 643.8149 | 0.22301 | 1.3157 | 181.0855 | 522.7434
|  |  | 11.3333 | 696.9629 | 470.4819 | 645.7923 | 0.2228 | 1.3141 | 182.3995 | 523.241
|  |  | 11.4167 | 698.0487 | 473.4923 | 647.7832 | 0.22259 | 1.3125 | 183.7121 | 523.7364
|  |  | 11.5 | 699.1266 | 476.483 | 649.7874 | 0.22238 | 1.3109 | 185.023 | 524.2296
|  |  | 11.5833 | 700.1968 | 479.4539 | 651.8046 | 0.22217 | 1.3093 | 186.3323 | 524.7206
|  |  | 11.6667 | 701.2595 | 482.405 | 653.8345 | 0.22196 | 1.3077 | 187.6401 | 525.2095
|  |  | 11.75 | 702.3146 | 485.3362 | 655.8771 | 0.22175 | 1.3061 | 188.9462 | 525.6963
|  |  | 11.8333 | 703.3624 | 488.2476 | 657.9321 | 0.22155 | 1.3045 | 190.2507 | 526.181
|  |  | 11.9167 | 704.4029 | 491.139 | 659.9992 | 0.22135 | 1.3029 | 191.5535 | 526.6637
|  |  | 12 | 705.4362 | 494.0104 | 662.0781 | 0.22114 | 1.3012 | 192.8548 | 527.1443
|  |  | 12.0833 | 706.4625 | 496.8619 | 664.1688 | 0.22094 | 1.2996 | 194.1543 | 527.623
|  |  | 12.1667 | 707.4818 | 499.6933 | 666.2708 | 0.22074 | 1.2979 | 195.4522 | 528.0997
|  |  | 12.25 | 708.4941 | 502.5048 | 668.3839 | 0.22054 | 1.2962 | 196.7484 | 528.5745
|  |  | 12.3333 | 709.4997 | 505.2962 | 670.5079 | 0.22034 | 1.2945 | 198.043 | 529.0474
|  |  | 12.4167 | 710.4986 | 508.0676 | 672.6425 | 0.22015 | 1.2929 | 199.3358 | 529.5185
|  |  | 12.5 | 711.4909 | 510.819 | 674.7874 | 0.21995 | 1.2912 | 200.627 | 529.9877
|  |  | 12.5833 | 712.4766 | 513.5504 | 676.9424 | 0.21976 | 1.2895 | 201.9165 | 530.4552
|  |  | 12.6667 | 713.4559 | 516.2619 | 679.1071 | 0.21956 | 1.2878 | 203.2042 | 530.9208
|  |  | 12.75 | 714.4288 | 518.9534 | 681.2814 | 0.21937 | 1.286 | 204.4903 | 531.3848
|  |  | 12.8333 | 715.3955 | 521.625 | 683.4649 | 0.21918 | 1.2843 | 205.7746 | 531.847
|  |  | 12.9167 | 716.356 | 524.2767 | 685.6573 | 0.21899 | 1.2826 | 207.0572 | 532.3075
|  |  | 13 | 717.3103 | 526.9086 | 687.8583 | 0.2188 | 1.2809 | 208.3381 | 532.7664
|  |  | 13.0833 | 718.2586 | 529.5206 | 690.0677 | 0.21861 | 1.2791 | 209.6172 | 533.2237
|  |  | 13.1667 | 719.201 | 532.1129 | 692.2852 | 0.21842 | 1.2774 | 210.8945 | 533.6795
|  |  | 13.25 | 720.1374 | 534.6855 | 694.5105 | 0.21824 | 1.2756 | 212.1702 | 534.1336
|  |  | 13.3333 | 721.068 | 537.2385 | 696.7433 | 0.21805 | 1.2739 | 213.444 | 534.5862
|  |  | 13.4167 | 721.9929 | 539.7719 | 698.9832 | 0.21787 | 1.2721 | 214.7161 | 535.0374
|  |  | 13.5 | 722.9121 | 542.2858 | 701.2301 | 0.21768 | 1.2703 | 215.9864 | 535.487
|  |  | 13.5833 | 723.8258 | 544.7803 | 703.4836 | 0.2175 | 1.2685 | 217.255 | 535.9353
|  |  | 13.6667 | 724.7338 | 547.2554 | 705.7435 | 0.21732 | 1.2668 | 218.5218 | 536.3821
|  |  | 13.75 | 725.6364 | 549.7112 | 708.0094 | 0.21714 | 1.265 | 219.7867 | 536.8275
|  |  | 13.8333 | 726.5336 | 552.1477 | 710.2811 | 0.21696 | 1.2632 | 221.0499 | 537.2716
|  |  | 13.9167 | 727.4255 | 554.5652 | 712.5583 | 0.21678 | 1.2614 | 222.3113 | 537.7144
|  |  | 14 | 728.3121 | 556.9636 | 714.8407 | 0.2166 | 1.2596 | 223.5709 | 538.1558
|  |  | 14.0833 | 729.1934 | 559.3431 | 717.128 | 0.21642 | 1.2578 | 224.8287 | 538.596
|  |  | 14.1667 | 730.0696 | 561.7038 | 719.42 | 0.21624 | 1.256 | 226.0847 | 539.035
|  |  | 14.25 | 730.9408 | 564.0457 | 721.7164 | 0.21607 | 1.2542 | 227.3389 | 539.4727
|  |  | 14.3333 | 731.8068 | 566.3689 | 724.0168 | 0.21589 | 1.2524 | 228.5912 | 539.9093
|  |  | 14.4167 | 732.6679 | 568.6736 | 726.3211 | 0.21572 | 1.2505 | 229.8418 | 540.3447
|  |  | 14.5 | 733.5241 | 570.9598 | 728.629 | 0.21554 | 1.2487 | 231.0905 | 540.7789
|  |  | 14.5833 | 734.3754 | 573.2276 | 730.9402 | 0.21537 | 1.2469 | 232.3374 | 541.2121
|  |  | 14.6667 | 735.2219 | 575.4773 | 733.2544 | 0.2152 | 1.2451 | 233.5824 | 541.6442
|  |  | 14.75 | 736.0637 | 577.7088 | 735.5713 | 0.21503 | 1.2432 | 234.8256 | 542.0752
|  |  | 14.8333 | 736.9008 | 579.9223 | 737.8908 | 0.21486 | 1.2414 | 236.067 | 542.5052
|  |  | 14.9167 | 737.7332 | 582.1179 | 740.2126 | 0.21468 | 1.2395 | 237.3066 | 542.9342
|  |  | 15 | 738.561 | 584.2957 | 742.5364 | 0.21452 | 1.2377 | 238.5443 | 543.3622
|  |  | 15.0833 | 739.3842 | 586.4559 | 744.862 | 0.21435 | 1.2358 | 239.7801 | 543.7893
|  |  | 15.1667 | 740.203 | 588.5985 | 747.1891 | 0.21418 | 1.234 | 241.0141 | 544.2155
|  |  | 15.25 | 741.0173 | 590.7237 | 749.5176 | 0.21401 | 1.2321 | 242.2462 | 544.6407
|  |  | 15.3333 | 741.8272 | 592.8316 | 751.847 | 0.21384 | 1.2303 | 243.4765 | 545.0651
|  |  | 15.4167 | 742.6327 | 594.9223 | 754.1774 | 0.21368 | 1.2284 | 244.705 | 545.4887
|  |  | 15.5 | 743.434 | 596.9959 | 756.5083 | 0.21351 | 1.2266 | 245.9315 | 545.9114
|  |  | 15.5833 | 744.2309 | 599.0527 | 758.8396 | 0.21335 | 1.2247 | 247.1562 | 546.3333
|  |  | 15.6667 | 745.0237 | 601.0926 | 760.9693 | 0.21318 | 1.2228 | 248.3791 | 546.7544
|  |  | 15.75 | 745.8123 | 603.1164 | 762.3942 | 0.21302 | 1.221 | 249.6 | 547.1748
|  |  | 15.8333 | 746.5967 | 605.126 | 763.8521 | 0.21285 | 1.2191 | 250.8191 | 547.5945
|  |  | 15.9167 | 747.3771 | 607.1214 | 765.344 | 0.21269 | 1.2172 | 252.0363 | 548.0134
|  |  | 16 | 748.1535 | 609.1025 | 766.8709 | 0.21253 | 1.2153 | 253.2517 | 548.4317
|  |  | 16.0833 | 748.9258 | 611.0694 | 768.434 | 0.21237 | 1.2135 | 254.4651 | 548.8493
|  |  | 16.1667 | 749.6941 | 613.022 | 770.0343 | 0.2122 | 1.2116 | 255.6767 | 549.2663
|  |  | 16.25 | 750.4586 | 614.9603 | 771.6732 | 0.21204 | 1.2097 | 256.8864 | 549.6827
|  |  | 16.3333 | 751.2192 | 616.8842 | 773.3518 | 0.21188 | 1.2078 | 258.0943 | 550.0985
|  |  | 16.4167 | 751.9759 | 618.7938 | 775.0715 | 0.21172 | 1.2059 | 259.3002 | 550.5137
|  |  | 16.5 | 752.7288 | 620.689 | 776.8336 | 0.21156 | 1.204 | 260.5042 | 550.9284
|  |  | 16.5833 | 753.478 | 622.5698 | 778.6395 | 0.2114 | 1.2022 | 261.7064 | 551.3426
|  |  | 16.6667 | 754.2234 | 624.4361 | 780.4906 | 0.21124 | 1.2003 | 262.9067 | 551.7562
|  |  | 16.75 | 754.9652 | 626.288 | 782.3886 | 0.21109 | 1.1984 | 264.105 | 552.1694
|  |  | 16.8333 | 755.7032 | 628.1255 | 784.335 | 0.21093 | 1.1965 | 265.3015 | 552.5821
|  |  | 16.9167 | 756.4377 | 629.9485 | 786.3315 | 0.21077 | 1.1946 | 266.4961 | 552.9944
|  |  | 17 | 757.1686 | 631.7571 | 788.3799 | 0.21061 | 1.1927 | 267.6888 | 553.4063
|  |  | 17.0833 | 757.8959 | 633.5511 | 790.482 | 0.21046 | 1.1908 | 268.8796 | 553.8178
|  |  | 17.1667 | 758.6198 | 635.3307 | 792.6396 | 0.2103 | 1.1889 | 270.0685 | 554.2289
|  |  | 17.25 | 759.3401 | 637.0958 | 794.8549 | 0.21014 | 1.187 | 271.2554 | 554.6397
|  |  | 17.3333 | 760.057 | 638.8463 | 797.1298 | 0.20999 | 1.1851 | 272.4405 | 555.0501
|  |  | 17.4167 | 760.7705 | 640.5824 | 799.4667 | 0.20983 | 1.1832 | 273.6237 | 555.4603
|  |  | 17.5 | 761.4806 | 642.304 | 801.8677 | 0.20968 | 1.1813 | 274.805 | 555.8701
|  |  | 17.5833 | 762.1873 | 644.011 | 804.3353 | 0.20952 | 1.1794 | 275.9844 | 556.2797
|  |  | 17.6667 | 762.8908 | 645.7035 | 806.8721 | 0.20937 | 1.1775 | 277.1618 | 556.689
|  |  | 17.75 | 763.5909 | 647.3815 | 809.4807 | 0.20922 | 1.1756 | 278.3374 | 557.0981
|  |  | 17.8333 | 764.2878 | 649.045 | 812.1638 | 0.20906 | 1.1737 | 279.511 | 557.507
|  |  | 17.9167 | 764.9815 | 650.694 | 814.9244 | 0.20891 | 1.1717 | 280.6828 | 557.9156
|  |  | 18 | 765.672 | 652.3284 | 817.7656 | 0.20876 | 1.1698 | 281.8526 | 558.3241
|  |  | 18.0833 | 766.3593 | 653.9483 | 820.6905 | 0.2086 | 1.1679 | 283.0205 | 558.7325
|  |  | 18.1667 | 767.0434 | 655.5537 | 823.7027 | 0.20845 | 1.166 | 284.1866 | 559.1407
|  |  | 18.25 | 767.7245 | 657.1446 | 826.8055 | 0.2083 | 1.1641 | 285.3507 | 559.5488
|  |  | 18.3333 | 768.4025 | 658.7209 | 830.0029 | 0.20815 | 1.1622 | 286.5128 | 559.9568
|  |  | 18.4167 | 769.0774 | 660.2827 | 833.2987 | 0.20799 | 1.1603 | 287.6731 | 560.3647
|  |  | 18.5 | 769.7493 | 661.83 | 836.6972 | 0.20784 | 1.1584 | 288.8315 | 560.7725
|  |  | 18.5833 | 770.4182 | 663.3628 | 840.2027 | 0.20769 | 1.1564 | 289.9879 | 561.1803
|  |  | 18.6667 | 771.0841 | 664.881 | 843.8198 | 0.20754 | 1.1545 | 291.1425 | 561.5881
|  |  | 18.75 | 771.747 | 666.3848 | 847.5535 | 0.20739 | 1.1526 | 292.2951 | 561.9958
|  |  | 18.8333 | 772.4071 | 667.8739 | 851.4089 | 0.20724 | 1.1507 | 293.4458 | 562.4036
|  |  | 18.9167 | 773.0643 | 669.3486 | 855.3915 | 0.20709 | 1.1488 | 294.5946 | 562.8113
|  |  | 19 | 773.7185 | 670.8087 | 859.5071 | 0.20694 | 1.1469 | 295.7415 | 563.2192
|  |  | 19.0833 | 774.37 | 672.2542 | 863.7617 | 0.20679 | 1.145 | 296.8864 | 563.627
|  |  | 19.1667 | 775.0186 | 673.6852 | 868.1618 | 0.20664 | 1.143 | 298.0295 | 564.0349
|  |  | 19.25 | 775.6644 | 675.1016 | 872.7144 | 0.20649 | 1.1411 | 299.1706 | 564.4429
|  |  | 19.3333 | 776.3075 | 676.5035 | 877.4265 | 0.20634 | 1.1392 | 300.3098 | 564.8511
|  |  | 19.4167 | 776.9478 | 677.8907 | 882.306 | 0.20619 | 1.1373 | 301.4471 | 565.2593
|  |  | 19.5 | 777.5854 | 679.2634 | 887.361 | 0.20604 | 1.1354 | 302.5825 | 565.6676
|  |  | 19.5833 | 778.2203 | 680.6214 | 892.6001 | 0.20589 | 1.1335 | 303.7159 | 566.0762
|  |  | 19.6667 | 778.8525 | 681.9648 | 898.0327 | 0.20575 | 1.1315 | 304.8475 | 566.4848
|  |  | 19.75 | 779.482 | 683.2935 | 903.6684 | 0.2056 | 1.1296 | 305.9771 | 566.8937
|  |  | 19.8333 | 780.1089 | 684.6076 | 909.5177 | 0.20545 | 1.1277 | 307.1048 | 567.3027
|  |  | 19.9167 | 780.7332 | 685.9069 | 915.5917 | 0.2053 | 1.1258 | 308.2306 | 567.7119
|  |  | 20 | 781.3549 | 687.1915 | 921.9023 | 0.20515 | 1.1239 | 309.3545 | 568.1214
|  |  | 20.0833 | 781.9741 | 688.4614 | 928.4619 | 0.205 | 1.122 | 310.4764 | 568.5311
|  |  | 20.1667 | 782.5907 | 689.7164 | 935.2842 | 0.20486 | 1.12 | 311.5965 | 568.9411
|  |  | 20.25 | 783.2047 | 690.9566 | 942.3833 | 0.20471 | 1.1181 | 312.7146 | 569.3513
|  |  | 20.3333 | 783.8163 | 692.182 | 949.7747 | 0.20456 | 1.1162 | 313.8308 | 569.7618
|  |  | 20.4167 | 784.4254 | 693.3924 | 957.4748 | 0.20441 | 1.1143 | 314.9451 | 570.1725
|  |  | 20.5 | 785.032 | 694.5878 | 965.5012 | 0.20427 | 1.1124 | 316.0575 | 570.5836
|  |  | 20.5833 | 785.6361 | 695.7682 | 973.8725 | 0.20412 | 1.1105 | 317.168 | 570.995
|  |  | 20.6667 | 786.2379 | 696.9336 | 982.6089 | 0.20397 | 1.1086 | 318.2765 | 571.4067
|  |  | 20.75 | 786.8372 | 698.0838 | 991.7321 | 0.20383 | 1.1066 | 319.3832 | 571.8188
|  |  | 20.8333 | 787.4341 | 699.2188 | 1001.2652 | 0.20368 | 1.1047 | 320.4879 | 572.2312
|  |  | 20.9167 | 788.0287 | 700.3385 | 1011.2331 | 0.20353 | 1.1028 | 321.5907 | 572.644
|  |  | 21 | 788.6209 | 701.4429 | 1021.6625 | 0.20339 | 1.1009 | 322.6916 | 573.0572
|  |  | 21.0833 | 789.2108 | 702.5318 | 1032.5823 | 0.20324 | 1.099 | 323.7906 | 573.4708
|  |  | 21.1667 | 789.7984 | 703.6053 | 1044.0234 | 0.20309 | 1.0971 | 324.8877 | 573.8847
|  |  | 21.25 | 790.3837 | 704.6632 | 1056.0192 | 0.20295 | 1.0952 | 325.9828 | 574.2991
|  |  | 21.3333 | 790.9667 | 705.7054 | 1068.6057 | 0.2028 | 1.0933 | 327.0761 | 574.7139
|  |  | 21.4167 | 791.5474 | 706.7318 | 1081.8218 | 0.20265 | 1.0913 | 328.1674 | 575.1292
|  |  | 21.5 | 792.1259 | 707.7423 | 1095.7095 | 0.20251 | 1.0894 | 329.2569 | 575.5449
|  |  | 21.5833 | 792.7022 | 708.7369 | 1110.314 | 0.20236 | 1.0875 | 330.3444 | 575.9611
|  |  | 21.6667 | 793.2762 | 709.7154 | 1125.6846 | 0.20221 | 1.0856 | 331.43 | 576.3777
|  |  | 21.75 | 793.8481 | 710.6777 | 1141.8742 | 0.20207 | 1.0837 | 332.5137 | 576.7948
|  |  | 21.8333 | 794.4178 | 711.6236 | 1158.9406 | 0.20192 | 1.0818 | 333.5956 | 577.2125
|  |  | 21.9167 | 794.9854 | 712.5531 | 1176.9462 | 0.20178 | 1.0799 | 334.6755 | 577.6306
|  |  | 22 | 795.5508 | 713.466 | 1195.9588 | 0.20163 | 1.078 | 335.7535 | 578.0492
|  |  | 22.0833 | 796.1141 | 714.3622 | 1216.0519 | 0.20148 | 1.0761 | 336.8296 | 578.4684
|  |  | 22.1667 | 796.6752 | 715.2416 | 1237.3057 | 0.20134 | 1.0742 | 337.9037 | 578.8881
|  |  | 22.25 | 797.2343 | 716.104 | 1259.8073 | 0.20119 | 1.0723 | 338.976 | 579.3083
|  |  | 22.3333 | 797.7913 | 716.9493 | 1283.6515 | 0.20105 | 1.0704 | 340.0464 | 579.7292
|  |  | 22.4167 | 798.3462 | 717.7773 | 1308.9417 | 0.2009 | 1.0685 | 341.1149 | 580.1505
|  |  | 22.5 | 798.8991 | 718.588 | 1335.7905 | 0.20075 | 1.0666 | 342.1815 | 580.5725
|  |  | 22.5833 | 799.45 | 719.3811 | 1364.321 | 0.20061 | 1.0647 | 343.2462 | 580.995
|  |  | 22.6667 | 799.9988 | 720.1565 | 1394.6675 | 0.20046 | 1.0628 | 344.309 | 581.4182
|  |  | 22.75 | 800.5456 | 720.9141 | 1426.977 | 0.20032 | 1.0609 | 345.3699 | 581.8419
|  |  | 22.8333 | 801.0905 | 721.6537 | 1461.41 | 0.20017 | 1.059 | 346.4289 | 582.2662
|  |  | 22.9167 | 801.6333 | 722.3753 | 1498.1424 | 0.20002 | 1.0571 | 347.486 | 582.6912
|  |  | 23 | 802.1742 | 723.0786 | 1537.3667 | 0.19988 | 1.0552 | 348.5412 | 583.1168
|  |  | 23.0833 | 802.7132 | 723.7636 | 1579.2942 | 0.19973 | 1.0533 | 349.5945 | 583.5431
|  |  | 23.1667 | 803.2502 | 724.4302 | 1624.1563 | 0.19959 | 1.0514 | 350.646 | 583.9699
|  |  | 23.25 | 803.7854 | 725.0782 | 1672.207 | 0.19944 | 1.0495 | 351.6955 | 584.3975
|  |  | 23.3333 | 804.3186 | 725.7076 | 1723.7256 | 0.1993 | 1.0477 | 352.7432 | 584.8257
|  |  | 23.4167 | 804.8499 | 726.3183 | 1779.0185 | 0.19915 | 1.0458 | 353.7889 | 585.2546
|  |  | 23.5 | 805.3793 | 726.9101 | 1838.4229 | 0.199 | 1.0439 | 354.8328 | 585.6841
|  |  | 23.5833 | 805.9069 | 727.4832 | 1902.3095 | 0.19886 | 1.042 | 355.8748 | 586.1144
|  |  | 23.6667 | 806.4326 | 728.0374 | 1971.0866 | 0.19871 | 1.0401 | 356.9149 | 586.5453
|  |  | 23.75 | 806.9565 | 728.5728 | 2045.2035 | 0.19857 | 1.0382 | 357.9532 | 586.977
|  |  | 23.8333 | 807.4786 | 729.0894 | 2125.1553 | 0.19842 | 1.0364 | 358.9895 | 587.4093
|  |  | 23.9167 | 807.9988 | 729.5871 | 2211.4877 | 0.19827 | 1.0345 | 360.024 | 587.8424
|  |  | 24 | 808.5173 | 730.0662 | 2304.8026 | 0.19813 | 1.0326 | 361.0566 | 588.2762
|  |  | 24.0833 | 809.0339 | 730.5266 | 2405.7637 | 0.19798 | 1.0307 | 362.0873 | 588.7107
|  |  | 24.1667 | 809.5488 | 730.9685 | 2515.1039 | 0.19784 | 1.0288 | 363.1161 | 589.146
|  |  | 24.25 | 810.0619 | 731.3921 | 2633.632 | 0.19769 | 1.027 | 364.1431 | 589.582
|  |  | 24.3333 | 810.5733 | 731.7975 | 2762.2417 | 0.19754 | 1.0251 | 365.1682 | 590.0187
|  |  | 24.4167 | 811.0829 | 732.1849 | 2901.9204 | 0.1974 | 1.0232 | 366.1914 | 590.4563
|  |  | 24.5 | 811.5908 | 732.5547 | 3053.7596 | 0.19725 | 1.0214 | 367.2128 | 590.8945
|  |  | 24.5833 | 812.097 | 732.9071 | 3218.9663 | 0.1971 | 1.0195 | 368.2323 | 591.3336
|  |  | 24.6667 | 812.6015 | 733.2424 | 3398.8759 | 0.19696 | 1.0176 | 369.2499 | 591.7734
|  |  | 24.75 | 813.1043 | 733.5609 | 3594.9663 | 0.19681 | 1.0158 | 370.2656 | 592.214
|  |  | 24.8333 | 813.6054 | 733.863 | 3808.8737 | 0.19666 | 1.0139 | 371.2795 | 592.6554
|  |  | 24.9167 | 814.1049 | 734.1492 | 4042.4101 | 0.19652 | 1.012 | 372.2915 | 593.0976
|  |  | 25 | 814.6026 | 734.4197 | 4297.5837 | 0.19637 | 1.0102 | 373.3017 | 593.5406
|  |  | 25.0833 | 815.0988 | 734.6752 | 4576.62 | 0.19623 | 1.0083 | 374.31 | 593.9844
|  |  | 25.1667 | 815.5933 | 734.916 | 4881.9871 | 0.19608 | 1.0064 | 375.3165 | 594.429
|  |  | 25.25 | 816.0861 | 735.1427 | 4846.5597 | 0.19593 | 1.0046 | 376.3211 | 594.8745
|  |  | 25.3333 | 816.5774 | 735.3719 | 4620.9915 | 0.19579 | 1.0027 | 377.3238 | 595.3207
|  |  | 25.4167 | 817.067 | 735.6134 | 4407.6849 | 0.19564 | 1.0009 | 378.3247 | 595.7678
|  |  | 25.5 | 817.5551 | 735.8675 | 4206.0377 | 0.19549 | 0.99903 | 379.3237 | 596.2157
|  |  | 25.5833 | 818.0415 | 736.1347 | 4015.4709 | 0.19534 | 0.99719 | 380.3209 | 596.6644
|  |  | 25.6667 | 818.5264 | 736.4157 | 3835.4282 | 0.1952 | 0.99534 | 381.3162 | 597.114
|  |  | 25.75 | 819.0098 | 736.7109 | 3665.3758 | 0.19505 | 0.99349 | 382.3097 | 597.5644
|  |  | 25.8333 | 819.4915 | 737.0207 | 3504.8018 | 0.1949 | 0.99165 | 383.3014 | 598.0157
|  |  | 25.9167 | 819.9718 | 737.3457 | 3353.2153 | 0.19476 | 0.98981 | 384.2912 | 598.4678
|  |  | 26 | 820.4505 | 737.6863 | 3210.1464 | 0.19461 | 0.98797 | 385.2791 | 598.9208
|  |  | 26.0833 | 820.9276 | 738.0431 | 3075.1453 | 0.19446 | 0.98613 | 386.2653 | 599.3747
|  |  | 26.1667 | 821.4033 | 738.4164 | 2947.7821 | 0.19432 | 0.98429 | 387.2496 | 599.8294
|  |  | 26.25 | 821.8774 | 738.8067 | 2827.6458 | 0.19417 | 0.98246 | 388.232 | 600.285
|  |  | 26.3333 | 822.3501 | 739.2145 | 2714.344 | 0.19402 | 0.98062 | 389.2126 | 600.7414
|  |  | 26.4167 | 822.8213 | 739.64 | 2607.5024 | 0.19387 | 0.97879 | 390.1914 | 601.1988
|  |  | 26.5 | 823.291 | 740.0837 | 2506.7643 | 0.19373 | 0.97696 | 391.1684 | 601.657
|  |  | 26.5833 | 823.7592 | 740.5458 | 2411.7897 | 0.19358 | 0.97514 | 392.1435 | 602.1161
|  |  | 26.6667 | 824.226 | 741.0267 | 2322.255 | 0.19343 | 0.97331 | 393.1168 | 602.5761
|  |  | 26.75 | 824.6913 | 741.5266 | 2237.8526 | 0.19328 | 0.97149 | 394.0883 | 603.037
|  |  | 26.8333 | 825.1551 | 742.0458 | 2158.2901 | 0.19314 | 0.96967 | 395.058 | 603.4987
|  |  | 26.9167 | 825.6176 | 742.5843 | 2083.2897 | 0.19299 | 0.96785 | 396.0258 | 603.9614
|  |  | 27 | 826.0786 | 743.1424 | 2012.588 | 0.19284 | 0.96603 | 396.9919 | 604.425
|  |  | 27.0833 | 826.5382 | 743.7201 | 1945.9351 | 0.19269 | 0.96421 | 397.9561 | 604.8895
|  |  | 27.1667 | 826.9964 | 744.3174 | 1883.0945 | 0.19254 | 0.9624 | 398.9185 | 605.3549
|  |  | 27.25 | 827.4532 | 744.9345 | 1823.842 | 0.1924 | 0.96059 | 399.8791 | 605.8212
|  |  | 27.3333 | 827.9086 | 745.5711 | 1767.9656 | 0.19225 | 0.95878 | 400.8379 | 606.2884
|  |  | 27.4167 | 828.3627 | 746.2273 | 1715.2651 | 0.1921 | 0.95697 | 401.7948 | 606.7565
|  |  | 27.5 | 828.8153 | 746.9029 | 1665.5513 | 0.19195 | 0.95517 | 402.75 | 607.2256
|  |  | 27.5833 | 829.2666 | 747.5977 | 1618.6454 | 0.1918 | 0.95336 | 403.7034 | 607.6955
|  |  | 27.6667 | 829.7166 | 748.3114 | 1574.3791 | 0.19165 | 0.95156 | 404.6549 | 608.1664
|  |  | 27.75 | 830.1652 | 749.0439 | 1532.5935 | 0.19151 | 0.94976 | 405.6047 | 608.6382
|  |  | 27.8333 | 830.6124 | 749.7947 | 1493.1389 | 0.19136 | 0.94797 | 406.5526 | 609.111
|  |  | 27.9167 | 831.0584 | 750.5636 | 1455.8747 | 0.19121 | 0.94617 | 407.4988 | 609.5846
|  |  | 28 | 831.503 | 751.3502 | 1420.6681 | 0.19106 | 0.94438 | 408.4432 | 610.0592
|  |  | 28.0833 | 831.9463 | 752.154 | 1387.3947 | 0.19091 | 0.94259 | 409.3858 | 610.5348
|  |  | 28.1667 | 832.3882 | 752.9746 | 1355.9373 | 0.19076 | 0.9408 | 410.3266 | 611.0112
|  |  | 28.25 | 832.8289 | 753.8115 | 1326.1859 | 0.19061 | 0.93901 | 411.2656 | 611.4886
|  |  | 28.3333 | 833.2683 | 754.6642 | 1298.0372 | 0.19047 | 0.93723 | 412.2028 | 611.967
|  |  | 28.4167 | 833.7064 | 755.5321 | 1271.3942 | 0.19032 | 0.93545 | 413.1383 | 612.4462
|  |  | 28.5 | 834.1432 | 756.4148 | 1246.1659 | 0.19017 | 0.93367 | 414.0719 | 612.9265
|  |  | 28.5833 | 834.5788 | 757.3116 | 1222.2671 | 0.19002 | 0.93189 | 415.0038 | 613.4076
|  |  | 28.6667 | 835.0131 | 758.222 | 1199.6177 | 0.18987 | 0.93012 | 415.934 | 613.8897
|  |  | 28.75 | 835.4461 | 759.1453 | 1178.1427 | 0.18972 | 0.92835 | 416.8623 | 614.3728
|  |  | 28.8333 | 835.8779 | 760.081 | 1157.7719 | 0.18957 | 0.92658 | 417.7889 | 614.8568
|  |  | 28.9167 | 836.3085 | 761.0283 | 1138.4394 | 0.18942 | 0.92481 | 418.7137 | 615.3417
|  |  | 29 | 836.7378 | 761.9868 | 1120.0836 | 0.18927 | 0.92304 | 419.6367 | 615.8276
|  |  | 29.0833 | 837.1659 | 762.9557 | 1102.6466 | 0.18912 | 0.92128 | 420.558 | 616.3145
|  |  | 29.1667 | 837.5928 | 763.9345 | 1086.0744 | 0.18897 | 0.91952 | 421.4775 | 616.8022
|  |  | 29.25 | 838.0184 | 764.9224 | 1070.3162 | 0.18883 | 0.91776 | 422.3953 | 617.291
|  |  | 29.3333 | 838.4429 | 765.9189 | 1055.3247 | 0.18868 | 0.91601 | 423.3113 | 617.7807
|  |  | 29.4167 | 838.8661 | 766.9234 | 1041.0553 | 0.18853 | 0.91425 | 424.2255 | 618.2713
|  |  | 29.5 | 839.2882 | 767.9352 | 1027.4664 | 0.18838 | 0.9125 | 425.138 | 618.7629
|  |  | 29.5833 | 839.7091 | 768.9537 | 1014.519 | 0.18823 | 0.91075 | 426.0488 | 619.2555
|  |  | 29.6667 | 840.1288 | 769.9784 | 1002.1766 | 0.18808 | 0.90901 | 426.9578 | 619.749
|  |  | 29.75 | 840.5473 | 771.0085 | 990.405 | 0.18793 | 0.90726 | 427.8651 | 620.2434
|  |  | 29.8333 | 840.9646 | 772.0436 | 979.172 | 0.18778 | 0.90552 | 428.7706 | 620.7389
|  |  | 29.9167 | 841.3808 | 773.0831 | 968.4476 | 0.18763 | 0.90378 | 429.6744 | 621.2352
|  |  | 30 | 841.7959 | 774.1264 | 958.2036 | 0.18748 | 0.90204 | 430.5764 | 621.7326
|  |  | 30.0833 | 842.2098 | 775.173 | 948.4137 | 0.18733 | 0.90031 | 431.4767 | 622.2308
|  |  | 30.1667 | 842.6225 | 776.2224 | 939.0529 | 0.18718 | 0.89858 | 432.3753 | 622.7301
|  |  | 30.25 | 843.0342 | 777.2739 | 930.0981 | 0.18703 | 0.89685 | 433.2722 | 623.2303
|  |  | 30.3333 | 843.4447 | 778.3272 | 921.5274 | 0.18688 | 0.89512 | 434.1673 | 623.7314
|  |  | 30.4167 | 843.854 | 779.3818 | 913.3204 | 0.18673 | 0.8934 | 435.0607 | 624.2335
|  |  | 30.5 | 844.2623 | 780.4371 | 905.4578 | 0.18658 | 0.89168 | 435.9524 | 624.7365
|  |  | 30.5833 | 844.6695 | 781.4928 | 897.9216 | 0.18643 | 0.88996 | 436.8423 | 625.2406
|  |  | 30.6667 | 845.0755 | 782.5484 | 890.6947 | 0.18628 | 0.88824 | 437.7306 | 625.7455
|  |  | 30.75 | 845.4804 | 783.6034 | 883.7613 | 0.18613 | 0.88653 | 438.6171 | 626.2514
|  |  | 30.8333 | 845.8843 | 784.6575 | 877.1063 | 0.18598 | 0.88482 | 439.5019 | 626.7583
|  |  | 30.9167 | 846.2871 | 785.7103 | 870.7156 | 0.18583 | 0.88311 | 440.385 | 627.2661
|  |  | 31 | 846.6888 | 786.7614 | 864.576 | 0.18568 | 0.8814 | 441.2664 | 627.7749
|  |  | 31.0833 | 847.0894 | 787.8104 | 858.6748 | 0.18552 | 0.8797 | 442.1461 | 628.2846
|  |  | 31.1667 | 847.4889 | 788.8571 | 853.0004 | 0.18537 | 0.878 | 443.0241 | 628.7953
|  |  | 31.25 | 847.8874 | 789.901 | 847.5417 | 0.18522 | 0.8763 | 443.9004 | 629.3069
|  |  | 31.3333 | 848.2849 | 790.9419 | 842.2881 | 0.18507 | 0.87461 | 444.775 | 629.8195
|  |  | 31.4167 | 848.6812 | 791.9794 | 837.2298 | 0.18492 | 0.87291 | 445.6479 | 630.333
|  |  | 31.5 | 849.0766 | 793.0133 | 832.3576 | 0.18477 | 0.87122 | 446.5192 | 630.8475
|  |  | 31.5833 | 849.4709 | 794.0434 | 827.6625 | 0.18462 | 0.86954 | 447.3887 | 631.3629
|  |  | 31.6667 | 849.8641 | 795.0693 | 823.1365 | 0.18447 | 0.86785 | 448.2566 | 631.8793
|  |  | 31.75 | 850.2564 | 796.0908 | 818.7715 | 0.18432 | 0.86617 | 449.1227 | 632.3966
|  |  | 31.8333 | 850.6476 | 797.1077 | 814.5602 | 0.18417 | 0.86449 | 449.9872 | 632.9148
|  |  | 31.9167 | 851.0378 | 798.1198 | 810.4956 | 0.18402 | 0.86281 | 450.85 | 633.434
|  |  | 32 | 851.4269 | 799.1268 | 806.5711 | 0.18387 | 0.86114 | 451.7112 | 633.9542
|  |  | 32.0833 | 851.8151 | 800.1286 | 802.7804 | 0.18372 | 0.85947 | 452.5706 | 634.4752
|  |  | 32.1667 | 852.2023 | 801.125 | 799.1176 | 0.18357 | 0.8578 | 453.4284 | 634.9972
|  |  | 32.25 | 852.5884 | 802.1158 | 795.5771 | 0.18341 | 0.85613 | 454.2846 | 635.5202
|  |  | 32.3333 | 852.9736 | 803.1009 | 792.1535 | 0.18326 | 0.85447 | 455.1391 | 636.0441
|  |  | 32.4167 | 853.3578 | 804.0802 | 788.8418 | 0.18311 | 0.85281 | 455.9919 | 636.5689
|  |  | 32.5 | 853.741 | 805.0534 | 785.6372 | 0.18296 | 0.85115 | 456.843 | 637.0947
|  |  | 32.5833 | 854.1232 | 806.0205 | 782.5352 | 0.18281 | 0.8495 | 457.6925 | 637.6214
|  |  | 32.6667 | 854.5044 | 806.9813 | 779.5315 | 0.18266 | 0.84785 | 458.5404 | 638.149
|  |  | 32.75 | 854.8847 | 807.9357 | 776.6219 | 0.18251 | 0.8462 | 459.3866 | 638.6775
|  |  | 32.8333 | 855.2641 | 808.8837 | 773.8026 | 0.18236 | 0.84455 | 460.2311 | 639.207
|  |  | 32.9167 | 855.6424 | 809.8252 | 771.0699 | 0.18221 | 0.84291 | 461.074 | 639.7374
|  |  | 33 | 856.0198 | 810.76 | 768.4203 | 0.18206 | 0.84127 | 461.9153 | 640.2687
|  |  | 33.0833 | 856.3963 | 811.6881 | 765.8504 | 0.1819 | 0.83963 | 462.7549 | 640.801
|  |  | 33.1667 | 856.7718 | 812.6094 | 763.3571 | 0.18175 | 0.838 | 463.5929 | 641.3342
|  |  | 33.25 | 857.1464 | 813.5239 | 760.9374 | 0.1816 | 0.83636 | 464.4293 | 641.8682
|  |  | 33.3333 | 857.52 | 814.4316 | 758.5882 | 0.18145 | 0.83473 | 465.264 | 642.4032
|  |  | 33.4167 | 857.8927 | 815.3323 | 756.307 | 0.1813 | 0.83311 | 466.0971 | 642.9392
|  |  | 33.5 | 858.2645 | 816.226 | 754.0911 | 0.18115 | 0.83148 | 466.9286 | 643.476
|  |  | 33.5833 | 858.6354 | 817.1127 | 751.938 | 0.181 | 0.82986 | 467.7585 | 644.0137
|  |  | 33.6667 | 859.0054 | 817.9925 | 749.8453 | 0.18085 | 0.82824 | 468.5867 | 644.5524
|  |  | 33.75 | 859.3744 | 818.8652 | 747.8108 | 0.1807 | 0.82663 | 469.4133 | 645.0919
|  |  | 33.8333 | 859.7425 | 819.7308 | 745.8322 | 0.18054 | 0.82502 | 470.2384 | 645.6324
|  |  | 33.9167 | 860.1098 | 820.5894 | 743.9075 | 0.18039 | 0.82341 | 471.0618 | 646.1738
|  |  | 34 | 860.4761 | 821.4409 | 742.0348 | 0.18024 | 0.8218 | 471.8836 | 646.716
|  |  | 34.0833 | 860.8416 | 822.2853 | 740.2121 | 0.18009 | 0.8202 | 472.7038 | 647.2592
|  |  | 34.1667 | 861.2061 | 823.1227 | 738.4377 | 0.17994 | 0.8186 | 473.5224 | 647.8033
|  |  | 34.25 | 861.5698 | 823.953 | 736.7098 | 0.17979 | 0.817 | 474.3394 | 648.3482
|  |  | 34.3333 | 861.9326 | 824.7763 | 735.0267 | 0.17964 | 0.8154 | 475.1548 | 648.8941
|  |  | 34.4167 | 862.2945 | 825.5925 | 733.3869 | 0.17949 | 0.81381 | 475.9686 | 649.4408
|  |  | 34.5 | 862.6555 | 826.4018 | 731.7889 | 0.17934 | 0.81222 | 476.7808 | 649.9884
|  |  | 34.5833 | 863.0157 | 827.2041 | 730.2312 | 0.17918 | 0.81064 | 477.5914 | 650.5369
|  |  | 34.6667 | 863.375 | 827.9994 | 728.7124 | 0.17903 | 0.80905 | 478.4005 | 651.0863
|  |  | 34.75 | 863.7335 | 828.7878 | 727.2313 | 0.17888 | 0.80747 | 479.208 | 651.6366
|  |  | 34.8333 | 864.091 | 829.5694 | 725.7864 | 0.17873 | 0.8059 | 480.0139 | 652.1877
|  |  | 34.9167 | 864.4478 | 830.344 | 724.3767 | 0.17858 | 0.80432 | 480.8182 | 652.7398
|  |  | 35 | 864.8037 | 831.1119 | 723.0008 | 0.17843 | 0.80275 | 481.6209 | 653.2927
|  |  | 35.0833 | 865.1587 | 831.873 | 721.6578 | 0.17828 | 0.80118 | 482.4221 | 653.8464
|  |  | 35.1667 | 865.5129 | 832.6273 | 720.3465 | 0.17813 | 0.79962 | 483.2217 | 654.4011
|  |  | 35.25 | 865.8663 | 833.375 | 719.0659 | 0.17798 | 0.79805 | 484.0198 | 654.9565
|  |  | 35.3333 | 866.2189 | 834.1161 | 717.815 | 0.17783 | 0.7965 | 484.8163 | 655.5129
|  |  | 35.4167 | 866.5706 | 834.8505 | 716.5928 | 0.17767 | 0.79494 | 485.6112 | 656.0701
|  |  | 35.5 | 866.9215 | 835.5785 | 715.3984 | 0.17752 | 0.79339 | 486.4046 | 656.6282
|  |  | 35.5833 | 867.2716 | 836.2999 | 714.2309 | 0.17737 | 0.79183 | 487.1964 | 657.1871
|  |  | 35.6667 | 867.6208 | 837.0149 | 713.0895 | 0.17722 | 0.79029 | 487.9867 | 657.7469
|  |  | 35.75 | 867.9693 | 837.7236 | 711.9734 | 0.17707 | 0.78874 | 488.7755 | 658.3075
|  |  | 35.8333 | 868.3169 | 838.4259 | 710.8817 | 0.17692 | 0.7872 | 489.5627 | 658.869
|  |  | 35.9167 | 868.6637 | 839.122 | 709.8138 | 0.17677 | 0.78566 | 490.3483 | 659.4313
|  |  | 36 | 869.0098 | 839.8119 | 708.7688 | 0.17662 | 0.78413 | 491.1325 | 659.9945
|  |  | 36.0833 | 869.355 | 840.4957 | 707.7462 | 0.17647 | 0.78259 | 491.9151 | 660.5585
|  |  | 36.1667 | 869.6994 | 841.1733 | 706.7451 | 0.17632 | 0.78106 | 492.6961 | 661.1233
|  |  | 36.25 | 870.0431 | 841.845 | 705.7651 | 0.17617 | 0.77954 | 493.4757 | 661.689
|  |  | 36.3333 | 870.3859 | 842.5107 | 704.8053 | 0.17602 | 0.77801 | 494.2537 | 662.2555
|  |  | 36.4167 | 870.728 | 843.1705 | 703.8653 | 0.17587 | 0.77649 | 495.0302 | 662.8228
|  |  | 36.5 | 871.0693 | 843.8245 | 702.9444 | 0.17571 | 0.77498 | 495.8051 | 663.3909
|  |  | 36.5833 | 871.4099 | 844.4727 | 702.0421 | 0.17556 | 0.77346 | 496.5786 | 663.9599
|  |  | 36.6667 | 871.7496 | 845.1153 | 701.1579 | 0.17541 | 0.77195 | 497.3506 | 664.5297
|  |  | 36.75 | 872.0886 | 845.7522 | 700.2912 | 0.17526 | 0.77044 | 498.121 | 665.1003
|  |  | 36.8333 | 872.4268 | 846.3835 | 699.4415 | 0.17511 | 0.76894 | 498.8899 | 665.6717
|  |  | 36.9167 | 872.7643 | 847.0093 | 698.6083 | 0.17496 | 0.76743 | 499.6574 | 666.2439
|  |  | 37 | 873.101 | 847.6297 | 697.7912 | 0.17481 | 0.76593 | 500.4233 | 666.8169
|  |  | 37.0833 | 873.4369 | 848.2448 | 696.9897 | 0.17466 | 0.76444 | 501.1877 | 667.3907
|  |  | 37.1667 | 873.7721 | 848.8545 | 696.2034 | 0.17451 | 0.76294 | 501.9507 | 667.9654
|  |  | 37.25 | 874.1066 | 849.459 | 695.4318 | 0.17436 | 0.76145 | 502.7121 | 668.5408
|  |  | 37.3333 | 874.4403 | 850.0583 | 694.6746 | 0.17421 | 0.75997 | 503.4721 | 669.117
|  |  | 37.4167 | 874.7732 | 850.6525 | 693.9313 | 0.17406 | 0.75848 | 504.2306 | 669.694
|  |  | 37.5 | 875.1054 | 851.2416 | 693.2016 | 0.17391 | 0.757 | 504.9876 | 670.2718
|  |  | 37.5833 | 875.4369 | 851.8258 | 692.4851 | 0.17376 | 0.75552 | 505.7431 | 670.8504
|  |  | 37.6667 | 875.7677 | 852.4051 | 691.7814 | 0.17361 | 0.75405 | 506.4972 | 671.4297
|  |  | 37.75 | 876.0977 | 852.9795 | 691.0901 | 0.17346 | 0.75258 | 507.2497 | 672.0098
|  |  | 37.8333 | 876.427 | 853.5491 | 690.4111 | 0.17331 | 0.75111 | 508.0008 | 672.5907
|  |  | 37.9167 | 876.7556 | 854.114 | 689.7439 | 0.17316 | 0.74964 | 508.7505 | 673.1724
|  |  | 38 | 877.0834 | 854.6743 | 689.0882 | 0.17301 | 0.74818 | 509.4987 | 673.7549
|  |  | 38.0833 | 877.4106 | 855.2299 | 688.4437 | 0.17286 | 0.74672 | 510.2454 | 674.3381
|  |  | 38.1667 | 877.737 | 855.781 | 687.8102 | 0.17271 | 0.74526 | 510.9906 | 674.922
|  |  | 38.25 | 878.0627 | 856.3277 | 687.1872 | 0.17256 | 0.74381 | 511.7344 | 675.5068
|  |  | 38.3333 | 878.3878 | 856.8699 | 686.5747 | 0.17242 | 0.74236 | 512.4768 | 676.0923
|  |  | 38.4167 | 878.7121 | 857.4078 | 685.9723 | 0.17227 | 0.74091 | 513.2177 | 676.6785
|  |  | 38.5 | 879.0357 | 857.9415 | 685.3797 | 0.17212 | 0.73947 | 513.9572 | 677.2655
|  |  | 38.5833 | 879.3586 | 858.4709 | 684.7967 | 0.17197 | 0.73802 | 514.6952 | 677.8532
|  |  | 38.6667 | 879.6808 | 858.9961 | 684.223 | 0.17182 | 0.73659 | 515.4318 | 678.4417
|  |  | 38.75 | 880.0023 | 859.5172 | 683.6585 | 0.17167 | 0.73515 | 516.1669 | 679.0309
|  |  | 38.8333 | 880.3232 | 860.0343 | 683.1028 | 0.17152 | 0.73372 | 516.9007 | 679.6208
|  |  | 38.9167 | 880.6433 | 860.5474 | 682.5559 | 0.17137 | 0.73229 | 517.6329 | 680.2115
|  |  | 39 | 880.9628 | 861.0565 | 682.0173 | 0.17122 | 0.73086 | 518.3638 | 680.8029
|  |  | 39.0833 | 881.2816 | 861.5618 | 681.4871 | 0.17107 | 0.72944 | 519.0932 | 681.3951
|  |  | 39.1667 | 881.5997 | 862.0633 | 680.9648 | 0.17093 | 0.72802 | 519.8213 | 681.9879
|  |  | 39.25 | 881.9171 | 862.561 | 680.4505 | 0.17078 | 0.7266 | 520.5479 | 682.5815
|  |  | 39.3333 | 882.2339 | 863.055 | 679.9437 | 0.17063 | 0.72519 | 521.2731 | 683.1758
|  |  | 39.4167 | 882.55 | 863.5454 | 679.4445 | 0.17048 | 0.72378 | 521.9968 | 683.7708
|  |  | 39.5 | 882.8654 | 864.0322 | 678.9526 | 0.17033 | 0.72237 | 522.7192 | 684.3665
|  |  | 39.5833 | 883.1802 | 864.5154 | 678.4678 | 0.17018 | 0.72096 | 523.4402 | 684.9629
|  |  | 39.6667 | 883.4943 | 864.9951 | 677.9899 | 0.17004 | 0.71956 | 524.1597 | 685.56
|  |  | 39.75 | 883.8078 | 865.4714 | 677.5189 | 0.16989 | 0.71816 | 524.8779 | 686.1579
|  |  | 39.8333 | 884.1206 | 865.9443 | 677.0545 | 0.16974 | 0.71677 | 525.5947 | 686.7564
|  |  | 39.9167 | 884.4327 | 866.4139 | 676.5965 | 0.16959 | 0.71538 | 526.31 | 687.3556
|  |  | 40 | 884.7442 | 866.8802 | 676.145 | 0.16944 | 0.71399 | 527.024 | 687.9555
|  |  | 40.0833 | 885.0551 | 867.3432 | 675.6996 | 0.1693 | 0.7126 | 527.7366 | 688.5561
|  |  | 40.1667 | 885.3653 | 867.8031 | 675.2602 | 0.16915 | 0.71122 | 528.4478 | 689.1573
|  |  | 40.25 | 885.6749 | 868.2598 | 674.8268 | 0.169 | 0.70984 | 529.1577 | 689.7593
|  |  | 40.3333 | 885.9838 | 868.7135 | 674.3991 | 0.16885 | 0.70846 | 529.8661 | 690.3619
|  |  | 40.4167 | 886.2921 | 869.1641 | 673.9771 | 0.16871 | 0.70709 | 530.5732 | 690.9652
|  |  | 40.5 | 886.5998 | 869.6116 | 673.5606 | 0.16856 | 0.70571 | 531.2789 | 691.5691
|  |  | 40.5833 | 886.9068 | 870.0563 | 673.1495 | 0.16841 | 0.70435 | 531.9833 | 692.1737
|  |  | 40.6667 | 887.2132 | 870.498 | 672.7437 | 0.16826 | 0.70298 | 532.6863 | 692.779
|  |  | 40.75 | 887.519 | 870.9369 | 672.3431 | 0.16812 | 0.70162 | 533.3879 | 693.385
|  |  | 40.8333 | 887.8241 | 871.373 | 671.9475 | 0.16797 | 0.70026 | 534.0882 | 693.9916
|  |  | 40.9167 | 888.1287 | 871.8062 | 671.5569 | 0.16782 | 0.69891 | 534.7871 | 694.5988
|  |  | 41 | 888.4326 | 872.2368 | 671.1711 | 0.16768 | 0.69755 | 535.4846 | 695.2067
|  |  | 41.0833 | 888.7359 | 872.6646 | 670.7901 | 0.16753 | 0.6962 | 536.1808 | 695.8152
|  |  | 41.1667 | 889.0386 | 873.0898 | 670.4136 | 0.16738 | 0.69486 | 536.8757 | 696.4244
|  |  | 41.25 | 889.3407 | 873.5124 | 670.0418 | 0.16724 | 0.69351 | 537.5692 | 697.0342
|  |  | 41.3333 | 889.6421 | 873.9324 | 669.6743 | 0.16709 | 0.69217 | 538.2614 | 697.6447
|  |  | 41.4167 | 889.943 | 874.3499 | 669.3112 | 0.16694 | 0.69083 | 538.9522 | 698.2558
|  |  | 41.5 | 890.2433 | 874.7649 | 668.9524 | 0.1668 | 0.6895 | 539.6417 | 698.8675
|  |  | 41.5833 | 890.5429 | 875.1774 | 668.5977 | 0.16665 | 0.68817 | 540.3299 | 699.4798
|  |  | 41.6667 | 890.842 | 875.5875 | 668.2471 | 0.16651 | 0.68684 | 541.0167 | 700.0928
|  |  | 41.75 | 891.1405 | 875.9953 | 667.9006 | 0.16636 | 0.68551 | 541.7022 | 700.7063
|  |  | 41.8333 | 891.4383 | 876.4006 | 667.5579 | 0.16621 | 0.68419 | 542.3864 | 701.3205
|  |  | 41.9167 | 891.7356 | 876.8037 | 667.2191 | 0.16607 | 0.68287 | 543.0693 | 701.9353
|  |  | 42 | 892.0323 | 877.2045 | 666.8841 | 0.16592 | 0.68156 | 543.7508 | 702.5507
|  |  | 42.0833 | 892.3284 | 877.6031 | 666.5527 | 0.16578 | 0.68024 | 544.4311 | 703.1667
|  |  | 42.1667 | 892.624 | 877.9994 | 666.225 | 0.16563 | 0.67893 | 545.11 | 703.7833
|  |  | 42.25 | 892.9189 | 878.3936 | 665.9008 | 0.16549 | 0.67763 | 545.7876 | 704.4005
|  |  | 42.3333 | 893.2133 | 878.7857 | 665.58 | 0.16534 | 0.67632 | 546.464 | 705.0183
|  |  | 42.4167 | 893.507 | 879.1756 | 665.2627 | 0.1652 | 0.67502 | 547.139 | 705.6367
|  |  | 42.5 | 893.8003 | 879.5634 | 664.9488 | 0.16505 | 0.67372 | 547.8127 | 706.2557
|  |  | 42.5833 | 894.0929 | 879.9493 | 664.6381 | 0.16491 | 0.67243 | 548.4851 | 706.8752
|  |  | 42.6667 | 894.385 | 880.333 | 664.3306 | 0.16476 | 0.67113 | 549.1563 | 707.4954
|  |  | 42.75 | 894.6765 | 880.7149 | 664.0263 | 0.16462 | 0.66984 | 549.8261 | 708.1161
|  |  | 42.8333 | 894.9674 | 881.0947 | 663.725 | 0.16448 | 0.66856 | 550.4947 | 708.7373
|  |  | 42.9167 | 895.2578 | 881.4726 | 663.4269 | 0.16433 | 0.66727 | 551.1619 | 709.3592
|  |  | 43 | 895.5476 | 881.8487 | 663.1316 | 0.16419 | 0.66599 | 551.8279 | 709.9816
|  |  | 43.0833 | 895.8368 | 882.2228 | 662.8394 | 0.16404 | 0.66472 | 552.4926 | 710.6046
|  |  | 43.1667 | 896.1255 | 882.5951 | 662.55 | 0.1639 | 0.66344 | 553.1561 | 711.2281
|  |  | 43.25 | 896.4137 | 882.9656 | 662.2634 | 0.16376 | 0.66217 | 553.8183 | 711.8522
|  |  | 43.3333 | 896.7013 | 883.3343 | 661.9795 | 0.16361 | 0.6609 | 554.4792 | 712.4769
|  |  | 43.4167 | 896.9883 | 883.7013 | 661.6984 | 0.16347 | 0.65964 | 555.1388 | 713.102
|  |  | 43.5 | 897.2748 | 884.0665 | 661.42 | 0.16333 | 0.65838 | 555.7972 | 713.7278
|  |  | 43.5833 | 897.5607 | 884.43 | 661.1442 | 0.16318 | 0.65712 | 556.4543 | 714.3541
|  |  | 43.6667 | 897.8461 | 884.7918 | 660.8709 | 0.16304 | 0.65586 | 557.1101 | 714.9809
|  |  | 43.75 | 898.131 | 885.1519 | 660.6002 | 0.1629 | 0.65461 | 557.7648 | 715.6082
|  |  | 43.8333 | 898.4153 | 885.5104 | 660.332 | 0.16275 | 0.65336 | 558.4181 | 716.2361
|  |  | 43.9167 | 898.699 | 885.8673 | 660.0662 | 0.16261 | 0.65211 | 559.0702 | 716.8645
|  |  | 44 | 898.9823 | 886.2226 | 659.8029 | 0.16247 | 0.65086 | 559.7211 | 717.4935
|  |  | 44.0833 | 899.265 | 886.5763 | 659.5418 | 0.16233 | 0.64962 | 560.3707 | 718.1229
|  |  | 44.1667 | 899.5471 | 886.9285 | 659.2831 | 0.16218 | 0.64838 | 561.0191 | 718.7529
|  |  | 44.25 | 899.8288 | 887.2792 | 659.0267 | 0.16204 | 0.64715 | 561.6662 | 719.3834
|  |  | 44.3333 | 900.1099 | 887.6283 | 658.7725 | 0.1619 | 0.64591 | 562.3121 | 720.0144
|  |  | 44.4167 | 900.3905 | 887.976 | 658.5206 | 0.16176 | 0.64468 | 562.9568 | 720.6459
|  |  | 44.5 | 900.6705 | 888.3221 | 658.2708 | 0.16162 | 0.64346 | 563.6003 | 721.2779
|  |  | 44.5833 | 900.9501 | 888.6669 | 658.0231 | 0.16147 | 0.64223 | 564.2425 | 721.9105
|  |  | 44.6667 | 901.2291 | 889.0102 | 657.7775 | 0.16133 | 0.64101 | 564.8835 | 722.5435
|  |  | 44.75 | 901.5076 | 889.3521 | 657.534 | 0.16119 | 0.63979 | 565.5233 | 723.177
|  |  | 44.8333 | 901.7856 | 889.6927 | 657.2925 | 0.16105 | 0.63858 | 566.1619 | 723.811
|  |  | 44.9167 | 902.063 | 890.0318 | 657.053 | 0.16091 | 0.63737 | 566.7993 | 724.4455
|  |  | 45 | 902.34 | 890.3697 | 656.8155 | 0.16077 | 0.63616 | 567.4354 | 725.0805
|  |  | 45.0833 | 902.6164 | 890.7062 | 656.5799 | 0.16063 | 0.63495 | 568.0704 | 725.7159
|  |  | 45.1667 | 902.8924 | 891.0413 | 656.3462 | 0.16049 | 0.63375 | 568.7041 | 726.3519
|  |  | 45.25 | 903.1678 | 891.3752 | 656.1144 | 0.16035 | 0.63255 | 569.3367 | 726.9883
|  |  | 45.3333 | 903.4427 | 891.7078 | 655.8845 | 0.16021 | 0.63135 | 569.968 | 727.6252
|  |  | 45.4167 | 903.7171 | 892.0392 | 655.6563 | 0.16007 | 0.63015 | 570.5982 | 728.2625
|  |  | 45.5 | 903.991 | 892.3693 | 655.43 | 0.15993 | 0.62896 | 571.2271 | 728.9003
|  |  | 45.5833 | 904.2645 | 892.6981 | 655.2054 | 0.15979 | 0.62777 | 571.8549 | 729.5386
|  |  | 45.6667 | 904.5374 | 893.0258 | 654.9825 | 0.15965 | 0.62659 | 572.4815 | 730.1774
|  |  | 45.75 | 904.8098 | 893.3522 | 654.7613 | 0.15951 | 0.6254 | 573.1069 | 730.8166
|  |  | 45.8333 | 905.0817 | 893.6775 | 654.5419 | 0.15937 | 0.62422 | 573.7311 | 731.4562
|  |  | 45.9167 | 905.3532 | 894.0016 | 654.3241 | 0.15923 | 0.62304 | 574.3542 | 732.0963
|  |  | 46 | 905.6241 | 894.3246 | 654.1079 | 0.15909 | 0.62187 | 574.976 | 732.7369
|  |  | 46.0833 | 905.8946 | 894.6464 | 653.8933 | 0.15895 | 0.6207 | 575.5967 | 733.3778
|  |  | 46.1667 | 906.1645 | 894.9671 | 653.6803 | 0.15881 | 0.61953 | 576.2163 | 734.0193
|  |  | 46.25 | 906.434 | 895.2867 | 653.4689 | 0.15867 | 0.61836 | 576.8346 | 734.6611
|  |  | 46.3333 | 906.703 | 895.6052 | 653.259 | 0.15853 | 0.6172 | 577.4518 | 735.3034
|  |  | 46.4167 | 906.9715 | 895.9226 | 653.0507 | 0.15839 | 0.61604 | 578.0679 | 735.9462
|  |  | 46.5 | 907.2395 | 896.2389 | 652.8438 | 0.15826 | 0.61488 | 578.6828 | 736.5893
|  |  | 46.5833 | 907.5071 | 896.5542 | 652.6385 | 0.15812 | 0.61373 | 579.2965 | 737.2329
|  |  | 46.6667 | 907.7742 | 896.8684 | 652.4345 | 0.15798 | 0.61257 | 579.9091 | 737.8769
|  |  | 46.75 | 908.0408 | 897.1816 | 652.2321 | 0.15784 | 0.61142 | 580.5205 | 738.5213
|  |  | 46.8333 | 908.3069 | 897.4938 | 652.031 | 0.1577 | 0.61028 | 581.1308 | 739.1661
|  |  | 46.9167 | 908.5726 | 897.805 | 651.8313 | 0.15757 | 0.60913 | 581.7399 | 739.8114
|  |  | 47 | 908.8378 | 898.1152 | 651.633 | 0.15743 | 0.60799 | 582.3479 | 740.457
|  |  | 47.0833 | 909.1025 | 898.4244 | 651.4361 | 0.15729 | 0.60686 | 582.9547 | 741.1031
|  |  | 47.1667 | 909.3667 | 898.7326 | 651.2405 | 0.15715 | 0.60572 | 583.5605 | 741.7495
|  |  | 47.25 | 909.6305 | 899.0399 | 651.0463 | 0.15702 | 0.60459 | 584.1651 | 742.3964
|  |  | 47.3333 | 909.8939 | 899.3462 | 650.8533 | 0.15688 | 0.60346 | 584.7685 | 743.0436
|  |  | 47.4167 | 910.1567 | 899.6515 | 650.6617 | 0.15674 | 0.60233 | 585.3708 | 743.6913
|  |  | 47.5 | 910.4191 | 899.956 | 650.4713 | 0.15661 | 0.60121 | 585.972 | 744.3393
|  |  | 47.5833 | 910.6811 | 900.2595 | 650 | 0.15647 | 0.60009 | 586.5721 | 744.9877
|  |  | 47.6667 | 910.9425 | 900.5622 | 650 | 0.15634 | 0.59897 | 587.1711 | 745.6365
|  |  | 47.75 | 911.2036 | 900.864 | 650 | 0.1562 | 0.59785 | 587.769 | 746.2857
|  |  | 47.8333 | 911.4642 | 901.1648 | 650 | 0.15606 | 0.59674 | 588.3657 | 746.9353
|  |  | 47.9167 | 911.7243 | 901.4646 | 650 | 0.15593 | 0.59563 | 588.9613 | 747.5852
|  |  | 48 | 911.984 | 901.7634 | 650 | 0.15579 | 0.59452 | 589.5558 | 748.2355
|  |  | 48.0833 | 912.2432 | 902.0613 | 650 | 0.15566 | 0.59342 | 590.1493 | 748.8862
|  |  | 48.1667 | 912.502 | 902.3583 | 650 | 0.15552 | 0.59231 | 590.7416 | 749.5372
|  |  | 48.25 | 912.7603 | 902.6544 | 650 | 0.15539 | 0.59121 | 591.3328 | 750.1886
|  |  | 48.3333 | 913.0182 | 902.9495 | 650 | 0.15525 | 0.59012 | 591.9229 | 750.8404
|  |  | 48.4167 | 913.2756 | 903.2438 | 650 | 0.15512 | 0.58902 | 592.5119 | 751.4925
|  |  | 48.5 | 913.5326 | 903.5372 | 650 | 0.15498 | 0.58793 | 593.0999 | 752.145
|  |  | 48.5833 | 913.7892 | 903.8297 | 650 | 0.15485 | 0.58684 | 593.6867 | 752.7978
|  |  | 48.6667 | 914.0453 | 904.1214 | 650 | 0.15471 | 0.58576 | 594.2725 | 753.4509
|  |  | 48.75 | 914.301 | 904.4122 | 650 | 0.15458 | 0.58468 | 594.8571 | 754.1045
|  |  | 48.8333 | 914.5562 | 904.7022 | 650 | 0.15445 | 0.5836 | 595.4407 | 754.7583
|  |  | 48.9167 | 914.811 | 904.9913 | 650 | 0.15431 | 0.58252 | 596.0233 | 755.4125
|  |  | 49 | 915.0654 | 905.2797 | 650 | 0.15418 | 0.58144 | 596.6047 | 756.067
|  |  | 49.0833 | 915.3194 | 905.5672 | 650 | 0.15404 | 0.58037 | 597.1851 | 756.7219
|  |  | 49.1667 | 915.5729 | 905.8539 | 650 | 0.15391 | 0.5793 | 597.7644 | 757.3771
|  |  | 49.25 | 915.826 | 906.1398 | 650 | 0.15378 | 0.57823 | 598.3426 | 758.0326
|  |  | 49.3333 | 916.0787 | 906.425 | 650 | 0.15364 | 0.57717 | 598.9198 | 758.6884
|  |  | 49.4167 | 916.3309 | 906.7094 | 650 | 0.15351 | 0.57611 | 599.4959 | 759.3446
|  |  | 49.5 | 916.5827 | 906.993 | 650 | 0.15338 | 0.57505 | 600.0709 | 760.2658
|  |  | 49.5833 | 916.8341 | 907.2758 | 650 | 0.15319 | 0.5738 | 600.6447 | 760.6596
|  |  | 49.6667 | 917.0851 | 907.5579 | 650 | 0.15311 | 0.57294 | 601.2177 | 761.0561
|  |  | 49.75 | 917.3356 | 907.8393 | 650 | 0.15303 | 0.57207 | 601.7897 | 761.4554
|  |  | 49.8333 | 917.5858 | 908.1199 | 650 | 0.15295 | 0.57121 | 602.3609 | 761.8573
|  |  | 49.9167 | 917.8355 | 908.3998 | 650 | 0.15287 | 0.57034 | 602.9313 | 762.2621
|  |  | 50 | 918.0848 | 908.679 | 650 | 0.15279 | 0.56948 | 603.5008 | 762.6697
|  |  | 50.0833 | 918.3337 | 908.9575 | 650 | 0.15271 | 0.56861 | 604.0694 | 763.0801
|  |  | 50.1667 | 918.5822 | 909.2353 | 650 | 0.15263 | 0.56774 | 604.6371 | 763.4934
|  |  | 50.25 | 918.8302 | 909.5124 | 650 | 0.15255 | 0.56688 | 605.204 | 763.9096
|  |  | 50.3333 | 919.0779 | 909.7887 | 650 | 0.15246 | 0.56601 | 605.77 | 764.3287
|  |  | 50.4167 | 919.3251 | 910.0645 | 650 | 0.15238 | 0.56514 | 606.3352 | 764.7507
|  |  | 50.5 | 919.572 | 910.3395 | 650 | 0.15229 | 0.56428 | 606.8994 | 765.1758
|  |  | 50.5833 | 919.8184 | 910.6139 | 650 | 0.15221 | 0.56341 | 607.4628 | 765.6038
|  |  | 50.6667 | 920.0644 | 910.8876 | 650 | 0.15213 | 0.56254 | 608.0254 | 766.0349
|  |  | 50.75 | 920.3101 | 911.1606 | 650 | 0.15204 | 0.56167 | 608.5871 | 766.4691
|  |  | 50.8333 | 920.5553 | 911.433 | 650 | 0.15195 | 0.5608 | 609.1479 | 766.9064
|  |  | 50.9167 | 920.8001 | 911.7048 | 650 | 0.15187 | 0.55993 | 609.7078 | 767.3468
|  |  | 51 | 921.0445 | 911.9759 | 650 | 0.15178 | 0.55906 | 610.2668 | 767.7903
|  |  | 51.0833 | 921.2886 | 912.2464 | 650 | 0.15169 | 0.55819 | 610.825 | 768.2371
|  |  | 51.1667 | 921.5322 | 912.5163 | 650 | 0.1516 | 0.55732 | 611.3824 | 768.6871
|  |  | 51.25 | 921.7754 | 912.7855 | 650 | 0.15152 | 0.55645 | 611.9388 | 769.1404
|  |  | 51.3333 | 922.0183 | 913.0542 | 650 | 0.15143 | 0.55558 | 612.4944 | 769.597
|  |  | 51.4167 | 922.2607 | 913.3222 | 650 | 0.15134 | 0.55471 | 613.0491 | 770.0569
|  |  | 51.5 | 922.5028 | 913.5896 | 650 | 0.15125 | 0.55383 | 613.6029 | 770.5201
|  |  | 51.5833 | 922.7444 | 913.8565 | 650 | 0.15115 | 0.55296 | 614.1559 | 770.9868
|  |  | 51.6667 | 922.9857 | 914.1227 | 650 | 0.15106 | 0.55209 | 614.708 | 771.4569
|  |  | 51.75 | 923.2266 | 914.3883 | 650 | 0.15097 | 0.55121 | 615.2592 | 771.9305
|  |  | 51.8333 | 923.4671 | 914.6534 | 650 | 0.15088 | 0.55034 | 615.8095 | 772.4076
|  |  | 51.9167 | 923.7072 | 914.9178 | 650 | 0.15079 | 0.54946 | 616.359 | 772.8883
|  |  | 52 | 923.9469 | 915.1817 | 650 | 0.15069 | 0.54859 | 616.9076 | 773.3725
|  |  | 52.0833 | 924.1863 | 915.4451 | 650 | 0.1506 | 0.54771 | 617.4553 | 773.8604
|  |  | 52.1667 | 924.4253 | 915.7078 | 650 | 0.1505 | 0.54684 | 618.0021 | 774.3519
|  |  | 52.25 | 924.6638 | 915.97 | 650 | 0.15041 | 0.54596 | 618.5481 | 774.8471
|  |  | 52.3333 | 924.902 | 916.2317 | 650 | 0.15031 | 0.54508 | 619.0932 | 775.3461
|  |  | 52.4167 | 925.1399 | 916.4928 | 650 | 0.15021 | 0.5442 | 619.6374 | 775.8489
|  |  | 52.5 | 925.3773 | 916.7533 | 650 | 0.15012 | 0.54332 | 620.1807 | 776.3554
|  |  | 52.5833 | 925.6144 | 917.0133 | 650 | 0.15002 | 0.54244 | 620.7231 | 776.8658
|  |  | 52.6667 | 925.8511 | 917.2728 | 650 | 0.14992 | 0.54156 | 621.2647 | 777.3802
|  |  | 52.75 | 926.0874 | 917.5317 | 650 | 0.14982 | 0.54068 | 621.8054 | 777.8985
|  |  | 52.8333 | 926.3234 | 917.7901 | 650 | 0.14972 | 0.5398 | 622.3452 | 778.4207
|  |  | 52.9167 | 926.559 | 918.048 | 650 | 0.14962 | 0.53892 | 622.8841 | 778.947
|  |  | 53 | 926.7942 | 918.3053 | 650 | 0.14952 | 0.53804 | 623.4221 | 779.4774
|  |  | 53.0833 | 927.029 | 918.5621 | 650 | 0.14942 | 0.53716 | 623.9593 | 780.0119
|  |  | 53.1667 | 927.2635 | 918.8184 | 650 | 0.14932 | 0.53627 | 624.4956 | 780.5506
|  |  | 53.25 | 927.4976 | 919.0742 | 650 | 0.14921 | 0.53539 | 625.031 | 781.0935
|  |  | 53.3333 | 927.7314 | 919.3295 | 650 | 0.14911 | 0.5345 | 625.5655 | 781.6406
|  |  | 53.4167 | 927.9647 | 919.5842 | 650 | 0.149 | 0.53362 | 626.0991 | 782.1921
|  |  | 53.5 | 928.1978 | 919.8385 | 650 | 0.1489 | 0.53273 | 626.6318 | 782.7479
|  |  | 53.5833 | 928.4304 | 920.0923 | 650 | 0.14879 | 0.53184 | 627.1636 | 783.3081
|  |  | 53.6667 | 928.6627 | 920.3455 | 650 | 0.14869 | 0.53096 | 627.6946 | 783.8727
|  |  | 53.75 | 928.8947 | 920.5983 | 650 | 0.14858 | 0.53007 | 628.2247 | 784.4419
|  |  | 53.8333 | 929.1262 | 920.8506 | 650 | 0.14847 | 0.52918 | 628.7538 | 785.0156
|  |  | 53.9167 | 929.3575 | 921.1024 | 650 | 0.14836 | 0.52829 | 629.2821 | 785.594
|  |  | 54 | 929.5883 | 921.3537 | 650 | 0.14825 | 0.5274 | 629.8095 | 786.1769
|  |  | 54.0833 | 929.8188 | 921.6045 | 650 | 0.14814 | 0.52651 | 630.336 | 786.7646
|  |  | 54.1667 | 930.049 | 921.8548 | 650 | 0.14803 | 0.52561 | 630.8616 | 787.3571
|  |  | 54.25 | 930.2788 | 922.1047 | 650 | 0.14792 | 0.52472 | 631.3864 | 787.9544
|  |  | 54.3333 | 930.5082 | 922.3541 | 650 | 0.14781 | 0.52383 | 631.9102 | 788.5565
|  |  | 54.4167 | 930.7373 | 922.603 | 650 | 0.1477 | 0.52293 | 632.4331 | 789.1636
|  |  | 54.5 | 930.9661 | 922.8515 | 650 | 0.14758 | 0.52203 | 632.9552 | 789.7757
|  |  | 54.5833 | 931.1945 | 923.0995 | 650 | 0.14747 | 0.52114 | 633.4763 | 790.3928
|  |  | 54.6667 | 931.4226 | 923.347 | 650 | 0.14735 | 0.52024 | 633.9965 | 791.0151
|  |  | 54.75 | 931.6503 | 923.5941 | 650 | 0.14724 | 0.51934 | 634.5159 | 791.6425
|  |  | 54.8333 | 931.8776 | 923.8407 | 650 | 0.14712 | 0.51844 | 635.0343 | 792.2751
|  |  | 54.9167 | 932.1046 | 924.0869 | 650 | 0.147 | 0.51754 | 635.5519 | 792.913
|  |  | 55 | 932.3313 | 924.3326 | 650 | 0.14689 | 0.51664 | 636.0685 | 793.5563
|  |  | 55.0833 | 932.5576 | 924.5778 | 650 | 0.14677 | 0.51574 | 636.5842 | 794.2049
|  |  | 55.1667 | 932.7836 | 924.8227 | 650 | 0.14665 | 0.51483 | 637.0991 | 794.8591
|  |  | 55.25 | 933.0093 | 925.067 | 650 | 0.14653 | 0.51393 | 637.613 | 795.5188
|  |  | 55.3333 | 933.2346 | 925.311 | 650 | 0.1464 | 0.51303 | 638.126 | 796.1841
|  |  | 55.4167 | 933.4596 | 925.5544 | 650 | 0.14628 | 0.51212 | 638.6381 | 796.855
|  |  | 55.5 | 933.6842 | 925.7975 | 650 | 0.14616 | 0.51121 | 639.1494 | 797.5318
|  |  | 55.5833 | 933.9085 | 926.0401 | 650 | 0.14604 | 0.5103 | 639.6597 | 798.2143
|  |  | 55.6667 | 934.1325 | 926.2823 | 650 | 0.14591 | 0.50939 | 640.1691 | 798.9027
|  |  | 55.75 | 934.3561 | 926.524 | 650 | 0.14578 | 0.50848 | 640.6775 | 799.5971
|  |  | 55.8333 | 934.5794 | 926.7654 | 650 | 0.14566 | 0.50757 | 641.1851 | 800.2975
|  |  | 55.9167 | 934.8024 | 927.0063 | 650 | 0.14553 | 0.50666 | 641.6918 | 801.004
|  |  | 56 | 935.025 | 927.2467 | 650 | 0.1454 | 0.50574 | 642.1975 | 801.7167
|  |  | 56.0833 | 935.2473 | 927.4868 | 650 | 0.14527 | 0.50483 | 642.7023 | 802.4357
|  |  | 56.1667 | 935.4693 | 927.7264 | 650 | 0.14514 | 0.50391 | 643.2062 | 803.1609
|  |  | 56.25 | 935.6909 | 927.9656 | 650 | 0.14501 | 0.50299 | 643.7092 | 803.8926
|  |  | 56.3333 | 935.9122 | 928.2044 | 650 | 0.14488 | 0.50208 | 644.2113 | 804.6308
|  |  | 56.4167 | 936.1332 | 928.4428 | 650 | 0.14475 | 0.50116 | 644.7125 | 805.3755
|  |  | 56.5 | 936.3539 | 928.6808 | 650 | 0.14461 | 0.50023 | 645.2127 | 806.1269
|  |  | 56.5833 | 936.5742 | 928.9183 | 650 | 0.14448 | 0.49931 | 645.712 | 806.8851
|  |  | 56.6667 | 936.7942 | 929.1555 | 650 | 0.14434 | 0.49839 | 646.2104 | 807.65
|  |  | 56.75 | 937.0139 | 929.3922 | 650 | 0.14421 | 0.49746 | 646.7079 | 808.4219
|  |  | 56.8333 | 937.2333 | 929.6286 | 650 | 0.14407 | 0.49654 | 647.2044 | 809.2008
|  |  | 56.9167 | 937.4524 | 929.8645 | 650 | 0.14393 | 0.49561 | 647.7 | 809.9867
|  |  | 57 | 937.6711 | 930.1 | 650 | 0.14379 | 0.49468 | 648.1947 | 810.7799
|  |  | 57.0833 | 937.8895 | 930.3352 | 650 | 0.14365 | 0.49375 | 648.6884 | 811.5803
|  |  | 57.1667 | 938.1076 | 930.5699 | 650 | 0.14351 | 0.49281 | 649.1813 | 812.388
|  |  | 57.25 | 938.3254 | 930.8043 | 650 | 0.14336 | 0.49188 | 649.6731 | 813.2032
|  |  | 57.3333 | 938.5428 | 931.0382 | 650 | 0.14322 | 0.49095 | 650.1641 | 814.026
|  |  | 57.4167 | 938.76 | 931.2718 | 650 | 0.14308 | 0.49001 | 650.6541 | 814.8564
|  |  | 57.5 | 938.9768 | 931.505 | 650 | 0.14293 | 0.48907 | 651.1432 | 815.6946
|  |  | 57.5833 | 939.1933 | 931.7377 | 650 | 0.14278 | 0.48813 | 651.6313 | 816.5406
|  |  | 57.6667 | 939.4095 | 931.9701 | 650 | 0.14264 | 0.48719 | 652.1185 | 817.3946
|  |  | 57.75 | 939.6254 | 932.2022 | 650 | 0.14249 | 0.48625 | 652.6047 | 818.2567
|  |  | 57.8333 | 939.841 | 932.4338 | 650 | 0.14234 | 0.4853 | 653.09 | 819.1269
|  |  | 57.9167 | 940.0563 | 932.665 | 650 | 0.14219 | 0.48436 | 653.5744 | 820.0054
|  |  | 58 | 940.2713 | 932.8959 | 650 | 0.14203 | 0.48341 | 654.0578 | 820.8923
|  |  | 58.0833 | 940.4859 | 933.1264 | 650 | 0.14188 | 0.48246 | 654.5402 | 821.7877
|  |  | 58.1667 | 940.7003 | 933.3565 | 650 | 0.14172 | 0.48151 | 655.0217 | 822.6917
|  |  | 58.25 | 940.9143 | 933.5862 | 650 | 0.14157 | 0.48055 | 655.5023 | 823.6044
|  |  | 58.3333 | 941.1281 | 933.8156 | 650 | 0.14141 | 0.4796 | 655.9819 | 824.526
|  |  | 58.4167 | 941.3415 | 934.0446 | 650 | 0.14125 | 0.47864 | 656.4605 | 825.4565
|  |  | 58.5 | 941.5546 | 934.2732 | 650 | 0.14109 | 0.47768 | 656.9382 | 826.3962
|  |  | 58.5833 | 941.7675 | 934.5014 | 650 | 0.14093 | 0.47672 | 657.4149 | 827.3451
|  |  | 58.6667 | 941.98 | 934.7293 | 650 | 0.14077 | 0.47576 | 657.8907 | 828.3033
|  |  | 58.75 | 942.1922 | 934.9568 | 650 | 0.14061 | 0.4748 | 658.3655 | 829.2709
|  |  | 58.8333 | 942.4041 | 935.184 | 650 | 0.14045 | 0.47383 | 658.8393 | 830.2482
|  |  | 58.9167 | 942.6158 | 935.4108 | 650 | 0.14028 | 0.47286 | 659.3122 | 831.2353
|  |  | 59 | 942.8271 | 935.6372 | 650 | 0.14011 | 0.47189 | 659.7841 | 832.2322
|  |  | 59.0833 | 943.0381 | 935.8632 | 650 | 0.13995 | 0.47092 | 660.255 | 833.2391
|  |  | 59.1667 | 943.2489 | 936.0889 | 650 | 0.13978 | 0.46995 | 660.7249 | 834.2561
|  |  | 59.25 | 943.4593 | 936.3143 | 650 | 0.13961 | 0.46897 | 661.1939 | 835.2835
|  |  | 59.3333 | 943.6694 | 936.5393 | 650 | 0.13943 | 0.46799 | 661.6619 | 836.3213
|  |  | 59.4167 | 943.8793 | 936.7639 | 650 | 0.13926 | 0.46701 | 662.1289 | 837.3696
|  |  | 59.5 | 944.0888 | 936.9882 | 650 | 0.13909 | 0.46603 | 662.5949 | 838.4288
|  |  | 59.5833 | 944.2981 | 937.2121 | 650 | 0.13891 | 0.46504 | 663.06 | 839.4988
|  |  | 59.6667 | 944.5071 | 937.4357 | 650 | 0.13873 | 0.46406 | 663.524 | 840.5798
|  |  | 59.75 | 944.7158 | 937.6589 | 650 | 0.13856 | 0.46307 | 663.9871 | 841.6721
|  |  | 59.8333 | 944.9241 | 937.8817 | 650 | 0.13838 | 0.46207 | 664.4492 | 842.7757
|  |  | 59.9167 | 945.1322 | 938.1043 | 650 | 0.1382 | 0.46108 | 664.9103 | 843.8909
|  |  | 60 | 945.3401 | 938.3264 | 650 | 0.13801 | 0.46008 | 665.3703 | 845.0178
|  |  | 60.0833 | 945.5476 | 938.5483 | 650 | 0.13783 | 0.45908 | 665.8294 | 846.1565
|  |  | 60.1667 | 945.7548 | 938.7698 | 650 | 0.13764 | 0.45808 | 666.2875 | 847.3073
|  |  | 60.25 | 945.9618 | 938.9909 | 650 | 0.13746 | 0.45708 | 666.7446 | 848.4704
|  |  | 60.3333 | 946.1684 | 939.2117 | 650 | 0.13727 | 0.45607 | 667.2007 | 849.6458
|  |  | 60.4167 | 946.3748 | 939.4322 | 650 | 0.13708 | 0.45506 | 667.6557 | 850.8338
|  |  | 60.5 | 946.5809 | 939.6523 | 650 | 0.13689 | 0.45405 | 668.1098 | 852.0346
|  |  | 60.5833 | 946.7867 | 939.8721 | 650 | 0.13669 | 0.45304 | 668.5628 | 853.2484
|  |  | 60.6667 | 946.9922 | 940.0915 | 650 | 0.1365 | 0.45202 | 669.0148 | 854.4753
|  |  | 60.75 | 947.1975 | 940.3107 | 650 | 0.1363 | 0.451 | 669.4659 | 855.7156
|  |  | 60.8333 | 947.4025 | 940.5294 | 650 | 0.13611 | 0.44998 | 669.9158 | 856.9695
|  |  | 60.9167 | 947.6071 | 940.7479 | 650 | 0.13591 | 0.44896 | 670.3648 | 858.2372
|  |  | 61 | 947.8116 | 940.966 | 650 | 0.13571 | 0.44793 | 670.8127 | 859.5188
|  |  | 61.0833 | 948.0157 | 941.1838 | 650 | 0.1355 | 0.4469 | 671.2596 | 860.8146
|  |  | 61.1667 | 948.2195 | 941.4012 | 650 | 0.1353 | 0.44586 | 671.7055 | 862.1248
|  |  | 61.25 | 948.4231 | 941.6184 | 650 | 0.13509 | 0.44483 | 672.1503 | 863.4497
|  |  | 61.3333 | 948.6264 | 941.8352 | 650 | 0.13489 | 0.44379 | 672.5941 | 864.7894
|  |  | 61.4167 | 948.8294 | 942.0516 | 650 | 0.13468 | 0.44275 | 673.0368 | 866.1442
|  |  | 61.5 | 949.0322 | 942.2678 | 650 | 0.13447 | 0.4417 | 673.4785 | 867.5144
|  |  | 61.5833 | 949.2347 | 942.4836 | 650 | 0.13425 | 0.44065 | 673.9192 | 868.9001
|  |  | 61.6667 | 949.4369 | 942.6991 | 650 | 0.13404 | 0.4396 | 674.3588 | 870.3016
|  |  | 61.75 | 949.6388 | 942.9143 | 650 | 0.13382 | 0.43855 | 674.7973 | 871.7192
|  |  | 61.8333 | 949.8405 | 943.1291 | 650 | 0.13361 | 0.43749 | 675.2348 | 873.1531
|  |  | 61.9167 | 950.0418 | 943.3437 | 650 | 0.13339 | 0.43643 | 675.6713 | 874.6036
|  |  | 62 | 950.243 | 943.5579 | 650 | 0.13317 | 0.43536 | 676.1066 | 876.071
|  |  | 62.0833 | 950.4438 | 943.7718 | 650 | 0.13294 | 0.43429 | 676.5409 | 877.5554
|  |  | 62.1667 | 950.6444 | 943.9854 | 650 | 0.13272 | 0.43322 | 676.9741 | 879.0572
|  |  | 62.25 | 950.8447 | 944.1986 | 650 | 0.13249 | 0.43215 | 677.4063 | 880.5767
|  |  | 62.3333 | 951.0447 | 944.4116 | 650 | 0.13226 | 0.43107 | 677.8374 | 882.1142
|  |  | 62.4167 | 951.2445 | 944.6242 | 650 | 0.13203 | 0.42999 | 678.2674 | 883.6699
|  |  | 62.5 | 951.444 | 944.8366 | 650 | 0.1318 | 0.4289 | 678.6963 | 885.2442
|  |  | 62.5833 | 951.6433 | 945.0486 | 650 | 0.13157 | 0.42781 | 679.1241 | 886.8373
|  |  | 62.6667 | 951.8422 | 945.2603 | 650 | 0.13133 | 0.42672 | 679.5508 | 888.4495
|  |  | 62.75 | 952.041 | 945.4717 | 650 | 0.13109 | 0.42562 | 679.9764 | 890.0813
|  |  | 62.8333 | 952.2394 | 945.6827 | 650 | 0.13085 | 0.42452 | 680.4009 | 891.7328
|  |  | 62.9167 | 952.4376 | 945.8935 | 650 | 0.13061 | 0.42342 | 680.8244 | 893.4045
|  |  | 63 | 952.6355 | 946.104 | 650 | 0.13036 | 0.42231 | 681.2467 | 895.0967
|  |  | 63.0833 | 952.8332 | 946.3142 | 650 | 0.13012 | 0.4212 | 681.6679 | 896.8097
|  |  | 63.1667 | 953.0306 | 946.524 | 650 | 0.12987 | 0.42008 | 682.088 | 898.5438
|  |  | 63.25 | 953.2277 | 946.7336 | 650 | 0.12962 | 0.41896 | 682.5069 | 900.2995
|  |  | 63.3333 | 953.4246 | 946.9428 | 650 | 0.12937 | 0.41784 | 682.9248 | 902.077
|  |  | 63.4167 | 953.6213 | 947.1518 | 650 | 0.12911 | 0.41671 | 683.3415 | 903.8768
|  |  | 63.5 | 953.8176 | 947.3604 | 650 | 0.12885 | 0.41558 | 683.757 | 905.6993
|  |  | 63.5833 | 954.0137 | 947.5688 | 650 | 0.12859 | 0.41444 | 684.1715 | 907.5448
|  |  | 63.6667 | 954.2096 | 947.7768 | 650 | 0.12833 | 0.4133 | 684.5848 | 909.4138
|  |  | 63.75 | 954.4052 | 947.9846 | 650 | 0.12807 | 0.41215 | 684.9969 | 911.3066
|  |  | 63.8333 | 954.6006 | 948.192 | 650 | 0.1278 | 0.411 | 685.4079 | 913.2236
|  |  | 63.9167 | 954.7957 | 948.3992 | 650 | 0.12753 | 0.40985 | 685.8178 | 915.1654
|  |  | 64 | 954.9905 | 948.6061 | 650 | 0.12726 | 0.40869 | 686.2265 | 917.1322
|  |  | 64.0833 | 955.1851 | 948.8126 | 650 | 0.12699 | 0.40753 | 686.634 | 919.1247
|  |  | 64.1667 | 955.3794 | 949.0189 | 650 | 0.12672 | 0.40636 | 687.0404 | 921.1431
|  |  | 64.25 | 955.5735 | 949.2249 | 650 | 0.12644 | 0.40518 | 687.4456 | 923.188
|  |  | 64.3333 | 955.7673 | 949.4306 | 650 | 0.12616 | 0.40401 | 687.8496 | 925.2599
|  |  | 64.4167 | 955.9609 | 949.636 | 650 | 0.12588 | 0.40282 | 688.2524 | 927.3592
|  |  | 64.5 | 956.1542 | 949.8411 | 650 | 0.12559 | 0.40164 | 688.654 | 929.4865
|  |  | 64.5833 | 956.3473 | 950.0459 | 650 | 0.1253 | 0.40044 | 689.0545 | 931.6422
|  |  | 64.6667 | 956.5402 | 950.2504 | 650 | 0.12501 | 0.39925 | 689.4537 | 933.8268
|  |  | 64.75 | 956.7327 | 950.4547 | 650 | 0.12472 | 0.39804 | 689.8517 | 936.041
|  |  | 64.8333 | 956.9251 | 950.6586 | 650 | 0.12443 | 0.39683 | 690.2486 | 938.2851
|  |  | 64.9167 | 957.1172 | 950.8623 | 650 | 0.12413 | 0.39562 | 690.6442 | 940.5599
|  |  | 65 | 957.309 | 951.0657 | 650 | 0.12383 | 0.3944 | 691.0386 | 942.8657
|  |  | 65.0833 | 957.5006 | 951.2688 | 650 | 0.12353 | 0.39318 | 691.4318 | 945.2033
|  |  | 65.1667 | 957.692 | 951.4716 | 650 | 0.12322 | 0.39195 | 691.8237 | 947.5732
|  |  | 65.25 | 957.8831 | 951.6741 | 650 | 0.12291 | 0.39071 | 692.2144 | 949.976
|  |  | 65.3333 | 958.074 | 951.8764 | 650 | 0.1226 | 0.38947 | 692.6039 | 952.4124
|  |  | 65.4167 | 958.2646 | 952.0784 | 650 | 0.12229 | 0.38823 | 692.9921 | 954.8829
|  |  | 65.5 | 958.455 | 952.2801 | 650 | 0.12197 | 0.38697 | 693.3791 | 957.3882
|  |  | 65.5833 | 958.6451 | 952.4815 | 650 | 0.12165 | 0.38572 | 693.7648 | 959.9291
|  |  | 65.6667 | 958.835 | 952.6826 | 650 | 0.12133 | 0.38445 | 694.1493 | 962.506
|  |  | 65.75 | 959.0247 | 952.8835 | 650 | 0.121 | 0.38318 | 694.5325 | 965.1198
|  |  | 65.8333 | 959.2141 | 953.084 | 650 | 0.12068 | 0.38191 | 694.9144 | 967.7712
|  |  | 65.9167 | 959.4033 | 953.2843 | 650 | 0.12035 | 0.38063 | 695.295 | 970.4609
|  |  | 66 | 959.5922 | 953.4844 | 650 | 0.12001 | 0.37934 | 695.6743 | 973.1895
|  |  | 66.0833 | 959.7809 | 953.6841 | 650 | 0.11968 | 0.37804 | 696.0524 | 975.958
|  |  | 66.1667 | 959.9694 | 953.8836 | 650 | 0.11934 | 0.37674 | 696.4291 | 978.7671
|  |  | 66.25 | 960.1576 | 954.0828 | 650 | 0.11899 | 0.37544 | 696.8046 | 981.6175
|  |  | 66.3333 | 960.3456 | 954.2818 | 650 | 0.11865 | 0.37412 | 697.1787 | 984.5101
|  |  | 66.4167 | 960.5334 | 954.4804 | 650 | 0.1183 | 0.3728 | 697.5515 | 987.4457
|  |  | 66.5 | 960.7209 | 954.6788 | 650 | 0.11795 | 0.37148 | 697.923 | 990.4252
|  |  | 66.5833 | 960.9082 | 954.8769 | 650 | 0.11759 | 0.37014 | 698.2931 | 993.4494
|  |  | 66.6667 | 961.0952 | 955.0748 | 650 | 0.11724 | 0.3688 | 698.6619 | 996.5194
|  |  | 66.75 | 961.2821 | 955.2724 | 650 | 0.11687 | 0.36746 | 699.0294 | 999.6358
|  |  | 66.8333 | 961.4686 | 955.4697 | 650 | 0.11651 | 0.3661 | 699.3955 | 1002.7999
|  |  | 66.9167 | 961.655 | 955.6668 | 650 | 0.11614 | 0.36474 | 699.7602 | 1006.0124
|  |  | 67 | 961.8411 | 955.8635 | 650 | 0.11577 | 0.36338 | 700.1236 | 1009.2743
|  |  | 67.0833 | 962.027 | 956.0601 | 650 | 0.1154 | 0.362 | 700.4856 | 1012.5868
|  |  | 67.1667 | 962.2127 | 956.2563 | 650 | 0.11502 | 0.36062 | 700.8462 | 1015.9508
|  |  | 67.25 | 962.3981 | 956.4523 | 650 | 0.11464 | 0.35923 | 701.2054 | 1019.3674
|  |  | 67.3333 | 962.5833 | 956.648 | 650 | 0.11425 | 0.35783 | 701.5633 | 1022.8377
|  |  | 67.4167 | 962.7683 | 956.8435 | 650 | 0.11387 | 0.35643 | 701.9197 | 1026.3628
|  |  | 67.5 | 962.9531 | 957.0387 | 650 | 0.11348 | 0.35502 | 702.2747 | 1029.9439
|  |  | 67.5833 | 963.1376 | 957.2337 | 650 | 0.11308 | 0.3536 | 702.6283 | 1033.5821
|  |  | 67.6667 | 963.3219 | 957.4284 | 650 | 0.11268 | 0.35217 | 702.9805 | 1037.2787
|  |  | 67.75 | 963.5059 | 957.6228 | 650 | 0.11228 | 0.35074 | 703.3312 | 1041.0348
|  |  | 67.8333 | 963.6898 | 957.8169 | 650 | 0.11188 | 0.34929 | 703.6805 | 1044.8518
|  |  | 67.9167 | 963.8734 | 958.0109 | 650 | 0.11147 | 0.34784 | 704.0284 | 1048.731
|  |  | 68 | 964.0568 | 958.2045 | 650 | 0.11106 | 0.34639 | 704.3747 | 1052.6736
|  |  | 68.0833 | 964.24 | 958.3979 | 650 | 0.11064 | 0.34492 | 704.7197 | 1056.6811
|  |  | 68.1667 | 964.4229 | 958.591 | 650 | 0.11022 | 0.34344 | 705.0631 | 1060.7549
|  |  | 68.25 | 964.6056 | 958.7839 | 650 | 0.1098 | 0.34196 | 705.4051 | 1064.8964
|  |  | 68.3333 | 964.7881 | 958.9766 | 650 | 0.10937 | 0.34047 | 705.7455 | 1069.1071
|  |  | 68.4167 | 964.9704 | 959.1689 | 650 | 0.10894 | 0.33897 | 706.0845 | 1073.3884
|  |  | 68.5 | 965.1525 | 959.3611 | 650 | 0.1085 | 0.33746 | 706.422 | 1077.7421
|  |  | 68.5833 | 965.3343 | 959.5529 | 650 | 0.10807 | 0.33595 | 706.7579 | 1082.1696
|  |  | 68.6667 | 965.5159 | 959.7446 | 650 | 0.10762 | 0.33442 | 707.0924 | 1086.6726
|  |  | 68.75 | 965.6973 | 959.9359 | 650 | 0.10718 | 0.33289 | 707.4252 | 1091.2527
|  |  | 68.8333 | 965.8785 | 960.127 | 650 | 0.10673 | 0.33135 | 707.7566 | 1095.9118
|  |  | 68.9167 | 966.0594 | 960.3179 | 650 | 0.10627 | 0.3298 | 708.0864 | 1100.6516
|  |  | 69 | 966.2402 | 960.5085 | 650 | 0.10582 | 0.32824 | 708.4146 | 1105.4739
|  |  | 69.0833 | 966.4207 | 960.6989 | 650 | 0.10536 | 0.32667 | 708.7413 | 1110.3805
|  |  | 69.1667 | 966.601 | 960.889 | 650 | 0.10489 | 0.32509 | 709.0664 | 1115.3734
|  |  | 69.25 | 966.7811 | 961.0789 | 650 | 0.10442 | 0.3235 | 709.3899 | 1120.4547
|  |  | 69.3333 | 966.9609 | 961.2685 | 650 | 0.10395 | 0.32191 | 709.7118 | 1125.6262
|  |  | 69.4167 | 967.1406 | 961.4579 | 650 | 0.10347 | 0.3203 | 710.0321 | 1130.89
|  |  | 69.5 | 967.32 | 961.6471 | 650 | 0.10299 | 0.31869 | 710.3508 | 1136.2484
|  |  | 69.5833 | 967.4993 | 961.8359 | 650 | 0.1025 | 0.31706 | 710.6678 | 1141.7035
|  |  | 69.6667 | 967.6783 | 962.0246 | 650 | 0.10201 | 0.31543 | 710.9833 | 1147.2575
|  |  | 69.75 | 967.8571 | 962.213 | 650 | 0.10152 | 0.31379 | 711.2971 | 1152.9129
|  |  | 69.8333 | 968.0357 | 962.4012 | 650 | 0.10102 | 0.31214 | 711.6092 | 1158.6718
|  |  | 69.9167 | 968.214 | 962.5891 | 650 | 0.10052 | 0.31048 | 711.9197 | 1164.5369
|  |  | 70 | 968.3922 | 962.7768 | 650 | 0.10001 | 0.3088 | 712.2285 | 1170.5106
|  |  | 70.0833 | 968.5701 | 962.9642 | 650 | 0.099502 | 0.30712 | 712.5356 | 1176.5954
|  |  | 70.1667 | 968.7479 | 963.1514 | 650 | 0.098987 | 0.30543 | 712.841 | 1182.7942
|  |  | 70.25 | 968.9254 | 963.3384 | 650 | 0.098468 | 0.30373 | 713.1448 | 1189.1094
|  |  | 70.3333 | 969.1027 | 963.5251 | 650 | 0.097945 | 0.30202 | 713.4468 | 1195.5441
|  |  | 70.4167 | 969.2798 | 963.7116 | 650 | 0.097418 | 0.3003 | 713.7471 | 1202.1011
|  |  | 70.5 | 969.4567 | 963.8978 | 650 | 0.096887 | 0.29858 | 714.0457 | 1208.7832
|  |  | 70.5833 | 969.6334 | 964.0839 | 650 | 0.096351 | 0.29684 | 714.3425 | 1215.5937
|  |  | 70.6667 | 969.8099 | 964.2696 | 650 | 0.095811 | 0.29509 | 714.6376 | 1222.5355
|  |  | 70.75 | 969.9862 | 964.4552 | 650 | 0.095267 | 0.29333 | 714.9309 | 1229.612
|  |  | 70.8333 | 970.1622 | 964.6405 | 650 | 0.094719 | 0.29156 | 715.2225 | 1236.8264
|  |  | 70.9167 | 970.3381 | 964.8256 | 650 | 0.094167 | 0.28978 | 715.5123 | 1244.1822
|  |  | 71 | 970.5137 | 965.0104 | 650 | 0.09361 | 0.28799 | 715.8003 | 1251.6828
|  |  | 71.0833 | 970.6892 | 965.195 | 650 | 0.093049 | 0.28619 | 716.0865 | 1259.3319
|  |  | 71.1667 | 970.8644 | 965.3794 | 650 | 0.092484 | 0.28438 | 716.3708 | 1267.1331
|  |  | 71.25 | 971.0395 | 965.5635 | 650 | 0.091914 | 0.28257 | 716.6534 | 1275.0903
|  |  | 71.3333 | 971.2143 | 965.7474 | 650 | 0.091341 | 0.28074 | 716.9342 | 1283.2075
|  |  | 71.4167 | 971.3889 | 965.9311 | 650 | 0.090763 | 0.2789 | 717.213 | 1291.4886
|  |  | 71.5 | 971.5633 | 966.1145 | 650 | 0.090181 | 0.27705 | 717.4901 | 1299.9378
|  |  | 71.5833 | 971.7376 | 966.2978 | 650 | 0.089595 | 0.27519 | 717.7653 | 1308.5593
|  |  | 71.6667 | 971.9116 | 966.4808 | 650 | 0.089005 | 0.27332 | 718.0386 | 1317.3577
|  |  | 71.75 | 972.0854 | 966.6635 | 650 | 0.08841 | 0.27145 | 718.3101 | 1326.3373
|  |  | 71.8333 | 972.259 | 966.8461 | 650 | 0.087812 | 0.26956 | 718.5796 | 1335.5029
|  |  | 71.9167 | 972.4324 | 967.0284 | 650 | 0.087209 | 0.26766 | 718.8473 | 1344.8593
|  |  | 72 | 972.6057 | 967.2104 | 650 | 0.086602 | 0.26575 | 719.113 | 1354.4113
|  |  | 72.0833 | 972.7787 | 967.3923 | 650 | 0.085991 | 0.26384 | 719.3769 | 1364.1641
|  |  | 72.1667 | 972.9515 | 967.5739 | 650 | 0.085377 | 0.26191 | 719.6388 | 1374.123
|  |  | 72.25 | 973.1241 | 967.7553 | 650 | 0.084758 | 0.25997 | 719.8988 | 1384.2932
|  |  | 72.3333 | 973.2965 | 967.9365 | 650 | 0.084135 | 0.25803 | 720.1568 | 1394.6803
|  |  | 72.4167 | 973.4687 | 968.1175 | 650 | 0.083509 | 0.25607 | 720.4129 | 1405.2901
|  |  | 72.5 | 973.6408 | 968.2982 | 650 | 0.082878 | 0.25411 | 720.667 | 1416.1284
|  |  | 72.5833 | 973.8126 | 968.4787 | 650 | 0.082244 | 0.25214 | 720.9191 | 1427.2013
|  |  | 72.6667 | 973.9842 | 968.659 | 650 | 0.081606 | 0.25015 | 721.1693 | 1438.5149
|  |  | 72.75 | 974.1557 | 968.8391 | 650 | 0.080964 | 0.24816 | 721.4174 | 1450.0758
|  |  | 72.8333 | 974.3269 | 969.0189 | 650 | 0.080318 | 0.24616 | 721.6636 | 1461.8905
|  |  | 72.9167 | 974.4979 | 969.1985 | 650 | 0.079669 | 0.24415 | 721.9077 | 1473.9658
|  |  | 73 | 974.6688 | 969.3779 | 650 | 0.079017 | 0.24214 | 722.1499 | 1486.3087
|  |  | 73.0833 | 974.8394 | 969.5571 | 650 | 0.07836 | 0.24011 | 722.39 | 1498.9264
|  |  | 73.1667 | 975.0099 | 969.7361 | 650 | 0.077701 | 0.23807 | 722.6281 | 1511.8265
|  |  | 73.25 | 975.1801 | 969.9148 | 650 | 0.077038 | 0.23603 | 722.8641 | 1525.0165
|  |  | 73.3333 | 975.3502 | 970.0934 | 650 | 0.076371 | 0.23398 | 723.0981 | 1538.5043
|  |  | 73.4167 | 975.5201 | 970.2717 | 650 | 0.075702 | 0.23192 | 723.33 | 1552.298
|  |  | 73.5 | 975.6898 | 970.4498 | 650 | 0.075029 | 0.22986 | 723.5598 | 1566.4061
|  |  | 73.5833 | 975.8593 | 970.6277 | 650 | 0.074353 | 0.22778 | 723.7876 | 1580.8371
|  |  | 73.6667 | 976.0286 | 970.8053 | 650 | 0.073675 | 0.2257 | 724.0133 | 1595.5999
|  |  | 73.75 | 976.1977 | 970.9828 | 650 | 0.072993 | 0.22362 | 724.237 | 1610.7037
|  |  | 73.8333 | 976.3666 | 971.16 | 650 | 0.072309 | 0.22152 | 724.4585 | 1626.1579
|  |  | 73.9167 | 976.5353 | 971.337 | 650 | 0.071621 | 0.21942 | 724.6779 | 1641.9722
|  |  | 74 | 976.7039 | 971.5138 | 650 | 0.070932 | 0.21731 | 724.8952 | 1658.1566
|  |  | 74.0833 | 976.8722 | 971.6904 | 650 | 0.070239 | 0.2152 | 725.1104 | 1674.7214
|  |  | 74.1667 | 977.0404 | 971.8668 | 650 | 0.069545 | 0.21308 | 725.3235 | 1691.6773
|  |  | 74.25 | 977.2084 | 972.043 | 650 | 0.068847 | 0.21096 | 725.5345 | 1709.0353
|  |  | 74.3333 | 977.3761 | 972.219 | 650 | 0.068148 | 0.20883 | 725.7433 | 1726.8065
|  |  | 74.4167 | 977.5437 | 972.3947 | 650 | 0.067447 | 0.2067 | 725.95 | 1745.0026
|  |  | 74.5 | 977.7111 | 972.5702 | 650 | 0.066744 | 0.20456 | 726.1545 | 1763.6356
|  |  | 74.5833 | 977.8784 | 972.7456 | 650 | 0.066038 | 0.20241 | 726.357 | 1782.7179
|  |  | 74.6667 | 978.0454 | 972.9207 | 650 | 0.065332 | 0.20027 | 726.5572 | 1802.2621
|  |  | 74.75 | 978.2123 | 973.0956 | 650 | 0.064623 | 0.19811 | 726.7553 | 1822.2814
|  |  | 74.8333 | 978.3789 | 973.2703 | 650 | 0.063913 | 0.19596 | 726.9513 | 1842.7893
|  |  | 74.9167 | 978.5454 | 973.4448 | 650 | 0.063202 | 0.1938 | 727.1451 | 1863.7997
|  |  | 75 | 978.7117 | 973.6191 | 650 | 0.062489 | 0.19164 | 727.3367 | 1885.327
|  |  | 75.1667 | 979.0437 | 973.9783 | 650 | 0.061776 | 0.37922 | 727.716 | 1930.2887
|  |  | 75.3333 | 979.375 | 974.3359 | 650 | 0.060337 | 0.37049 | 728.0864 | 1977.538
|  |  | 75.5 | 979.7056 | 974.692 | 650 | 0.058895 | 0.36176 | 728.4482 | 2027.2102
|  |  | 75.6667 | 980.0354 | 975.0467 | 650 | 0.057452 | 0.35302 | 728.8012 | 2079.4492
|  |  | 75.8333 | 980.3646 | 975.3999 | 650 | 0.056009 | 0.34429 | 729.1455 | 2134.408
|  |  | 76 | 980.693 | 975.7517 | 650 | 0.054567 | 0.33556 | 729.4811 | 2192.2491
|  |  | 76.1667 | 981.0206 | 976.1021 | 650 | 0.053127 | 0.32686 | 729.8079 | 2253.1455
|  |  | 76.3333 | 981.3476 | 976.4513 | 650 | 0.051691 | 0.31818 | 730.1261 | 2317.2811
|  |  | 76.5 | 981.6739 | 976.7991 | 650 | 0.05026 | 0.30953 | 730.4356 | 2384.8512
|  |  | 76.6667 | 981.9994 | 977.1458 | 650 | 0.048836 | 0.30093 | 730.7366 | 2456.0638
|  |  | 76.8333 | 982.3242 | 977.4912 | 650 | 0.04742 | 0.29237 | 731.0289 | 2531.1397
|  |  | 77 | 982.6484 | 977.8355 | 650 | 0.046014 | 0.28387 | 731.3128 | 2610.314
|  |  | 77.1667 | 982.9718 | 978.1786 | 650 | 0.044618 | 0.27543 | 731.5882 | 2693.8363
|  |  | 77.3333 | 983.2946 | 978.5206 | 650 | 0.043235 | 0.26707 | 731.8553 | 2781.9723
|  |  | 77.5 | 983.6166 | 978.8615 | 650 | 0.041865 | 0.25878 | 732.1141 | 2875.0043
|  |  | 77.6667 | 983.938 | 979.2014 | 650 | 0.04051 | 0.25059 | 732.3647 | 2973.2325
|  |  | 77.8333 | 984.2586 | 979.5402 | 650 | 0.039172 | 0.24249 | 732.6072 | 3076.976
|  |  | 78 | 984.5786 | 979.878 | 650 | 0.037851 | 0.23449 | 732.8417 | 3186.5739
|  |  | 78.1667 | 984.8979 | 980.2147 | 650 | 0.03655 | 0.2266 | 733.0683 | 3302.3871
|  |  | 78.3333 | 985.2165 | 980.5505 | 650 | 0.035268 | 0.21883 | 733.2871 | 3424.7988
|  |  | 78.5 | 985.5345 | 980.8854 | 650 | 0.034007 | 0.21118 | 733.4983 | 3554.2166
|  |  | 78.6667 | 985.8517 | 981.2193 | 650 | 0.032769 | 0.20366 | 733.7019 | 3691.074
|  |  | 78.8333 | 986.1683 | 981.5522 | 650 | 0.031554 | 0.19628 | 733.8982 | 3835.8313
|  |  | 79 | 986.4843 | 981.8843 | 650 | 0.030363 | 0.18904 | 734.0872 | 3988.9783
|  |  | 79.1667 | 986.7995 | 982.2154 | 650 | 0.029197 | 0.18195 | 734.2692 | 4151.0354
|  |  | 79.3333 | 987.1142 | 982.5457 | 650 | 0.028058 | 0.175 | 734.4442 | 4322.556
|  |  | 79.5 | 987.4281 | 982.8751 | 650 | 0.026944 | 0.16822 | 734.6124 | 4504.1282
|  |  | 79.6667 | 987.7414 | 983.2036 | 650 | 0.025858 | 0.16159 | 734.774 | 4696.3772
|  |  | 79.8333 | 988.054 | 983.5313 | 650 | 0.024799 | 0.15512 | 734.9291 | 4899.9679
|  |  | 80 | 988.366 | 983.8581 | 650 | 0.023769 | 0.14882 | 735.0779 | 4914.8491
|  |  | 80.1667 | 988.6774 | 984.1841 | 650 | 0.023697 | 0.14847 | 735.2264 | 4761.3379
|  |  | 80.3333 | 988.9881 | 984.5093 | 650 | 0.024461 | 0.15332 | 735.3797 | 4613.7375
|  |  | 80.5 | 989.2981 | 984.8337 | 650 | 0.025244 | 0.15828 | 735.538 | 4471.8218
|  |  | 80.6667 | 989.6075 | 985.1574 | 650 | 0.026045 | 0.16336 | 735.7014 | 4335.3731
|  |  | 80.8333 | 989.9163 | 985.4802 | 650 | 0.026865 | 0.16856 | 735.8699 | 4204.1814
|  |  | 81 | 990.2244 | 985.8022 | 650 | 0.027703 | 0.17387 | 736.0438 | 4078.0447
|  |  | 81.1667 | 990.5319 | 986.1235 | 650 | 0.02856 | 0.17929 | 736.2231 | 3956.7683
|  |  | 81.3333 | 990.8388 | 986.444 | 650 | 0.029435 | 0.18483 | 736.4079 | 3840.1645
|  |  | 81.5 | 991.145 | 986.7637 | 650 | 0.030329 | 0.19048 | 736.5984 | 3728.0527
|  |  | 81.6667 | 991.4507 | 987.0827 | 650 | 0.031241 | 0.19623 | 736.7946 | 3620.2589
|  |  | 81.8333 | 991.7557 | 987.401 | 650 | 0.032171 | 0.2021 | 736.9967 | 3516.6155
|  |  | 82 | 992.0601 | 987.7185 | 650 | 0.033119 | 0.20808 | 737.2048 | 3416.9612
|  |  | 82.1667 | 992.3638 | 988.0353 | 650 | 0.034085 | 0.21416 | 737.419 | 3321.1407
|  |  | 82.3333 | 992.667 | 988.3514 | 650 | 0.035069 | 0.22035 | 737.6393 | 3229.0043
|  |  | 82.5 | 992.9695 | 988.6668 | 650 | 0.036069 | 0.22664 | 737.866 | 3140.4083
|  |  | 82.6667 | 993.2714 | 988.9815 | 650 | 0.037087 | 0.23302 | 738.099 | 3055.2138
|  |  | 82.8333 | 993.5728 | 989.2954 | 650 | 0.038121 | 0.23951 | 738.3385 | 2973.2878
|  |  | 83 | 993.8735 | 989.6087 | 650 | 0.039171 | 0.24608 | 738.5846 | 2894.5016
|  |  | 83.1667 | 994.1736 | 989.9212 | 650 | 0.040238 | 0.25275 | 738.8373 | 2818.732
|  |  | 83.3333 | 994.4731 | 990.2331 | 650 | 0.041319 | 0.2595 | 739.0968 | 2745.86
|  |  | 83.5 | 994.772 | 990.5443 | 650 | 0.042416 | 0.26633 | 739.3632 | 2675.7714
|  |  | 83.6667 | 995.0703 | 990.8548 | 650 | 0.043527 | 0.27325 | 739.6364 | 2608.3561
|  |  | 83.8333 | 995.3681 | 991.1646 | 650 | 0.044652 | 0.28023 | 739.9166 | 2543.5086
|  |  | 84 | 995.6652 | 991.4738 | 650 | 0.04579 | 0.28729 | 740.2039 | 2481.1269
|  |  | 84.1667 | 995.9617 | 991.7823 | 650 | 0.046941 | 0.29442 | 740.4984 | 2421.1134
|  |  | 84.3333 | 996.2577 | 992.0901 | 650 | 0.048105 | 0.3016 | 740.8 | 2363.374
|  |  | 84.5 | 996.5531 | 992.3973 | 650 | 0.04928 | 0.30885 | 741.1088 | 2307.8184
|  |  | 84.6667 | 996.8479 | 992.7038 | 650 | 0.050467 | 0.31615 | 741.425 | 2254.3595
|  |  | 84.8333 | 997.1421 | 993.0096 | 650 | 0.051663 | 0.32349 | 741.7484 | 2202.9139
|  |  | 85 | 997.4358 | 993.3149 | 650 | 0.05287 | 0.33088 | 742.0793 | 2153.4014
|  |  | 85.1667 | 997.7288 | 993.6194 | 650 | 0.054085 | 0.3383 | 742.4176 | 2105.7448
|  |  | 85.3333 | 998.0213 | 993.9234 | 650 | 0.05531 | 0.34576 | 742.7634 | 2059.87
|  |  | 85.5 | 998.3132 | 994.2267 | 650 | 0.056541 | 0.35325 | 743.1166 | 2015.7059
|  |  | 85.6667 | 998.6046 | 994.5293 | 650 | 0.05778 | 0.36075 | 743.4774 | 1973.1839
|  |  | 85.8333 | 998.8954 | 994.8314 | 650 | 0.059025 | 0.36828 | 743.8457 | 1932.2386
|  |  | 86 | 999.1856 | 995.1328 | 650 | 0.060276 | 0.37582 | 744.2215 | 1892.8068
|  |  | 86.1667 | 999.4753 | 995.4336 | 650 | 0.061532 | 0.38336 | 744.6048 | 1854.8279
|  |  | 86.3333 | 999.7644 | 995.7337 | 650 | 0.062792 | 0.39091 | 744.9957 | 1818.2439
|  |  | 86.5 | 1000.053 | 996.0333 | 650 | 0.064055 | 0.39845 | 745.3942 | 1782.9988
|  |  | 86.6667 | 1000.341 | 996.3322 | 650 | 0.065321 | 0.40598 | 745.8002 | 1749.0392
|  |  | 86.8333 | 1000.6284 | 996.6306 | 650 | 0.06659 | 0.41351 | 746.2137 | 1716.3137
|  |  | 87 | 1000.9153 | 996.9283 | 650 | 0.067859 | 0.42101 | 746.6347 | 1684.7727
|  |  | 87.1667 | 1001.2017 | 997.2254 | 650 | 0.06913 | 0.42849 | 747.0632 | 1654.3692
|  |  | 87.3333 | 1001.4875 | 997.5219 | 650 | 0.0704 | 0.43594 | 747.4991 | 1625.0575
|  |  | 87.5 | 1001.7727 | 997.8178 | 650 | 0.07167 | 0.44336 | 747.9425 | 1596.7941
|  |  | 87.6667 | 1002.0574 | 998.1131 | 650 | 0.072938 | 0.45074 | 748.3932 | 1569.5372
|  |  | 87.8333 | 1002.3416 | 998.4078 | 650 | 0.074205 | 0.45808 | 748.8513 | 1543.2468
|  |  | 88 | 1002.6252 | 998.702 | 650 | 0.075469 | 0.46537 | 749.3167 | 1517.8843
|  |  | 88.1667 | 1002.9083 | 998.9955 | 650 | 0.07673 | 0.47262 | 749.7893 | 1493.4128
|  |  | 88.3333 | 1003.1909 | 999.2885 | 650 | 0.077988 | 0.47981 | 750.2691 | 1469.797
|  |  | 88.5 | 1003.473 | 999.5808 | 650 | 0.079241 | 0.48694 | 750.756 | 1447.003
|  |  | 88.6667 | 1003.7545 | 999.8726 | 650 | 0.080489 | 0.49401 | 751.25 | 1424.9982
|  |  | 88.8333 | 1004.0354 | 1000.1638 | 650 | 0.081732 | 0.50101 | 751.7511 | 1403.7515
|  |  | 89 | 1004.3159 | 1000.4545 | 650 | 0.082969 | 0.50795 | 752.259 | 1383.233
|  |  | 89.1667 | 1004.5958 | 1000.7445 | 650 | 0.0842 | 0.51482 | 752.7738 | 1363.414
|  |  | 89.3333 | 1004.8752 | 1001.034 | 650 | 0.085424 | 0.52161 | 753.2954 | 1344.267
|  |  | 89.5 | 1005.1541 | 1001.3229 | 650 | 0.08664 | 0.52832 | 753.8237 | 1325.7658
|  |  | 89.6667 | 1005.4325 | 1001.6113 | 650 | 0.087849 | 0.53495 | 754.3587 | 1307.885
|  |  | 89.8333 | 1005.7103 | 1001.8991 | 650 | 0.08905 | 0.5415 | 754.9002 | 1290.6005
|  |  | 90 | 1005.9877 | 1002.1863 | 650 | 0.090243 | 0.54797 | 755.4482 | 1273.889
|  |  | 90.1667 | 1006.2645 | 1002.473 | 650 | 0.091427 | 0.55434 | 756.0025 | 1257.7284
|  |  | 90.3333 | 1006.5408 | 1002.7591 | 650 | 0.092602 | 0.56063 | 756.5631 | 1242.0974
|  |  | 90.5 | 1006.8166 | 1003.0446 | 650 | 0.093767 | 0.56683 | 757.13 | 1226.9755
|  |  | 90.6667 | 1007.0919 | 1003.3296 | 650 | 0.094923 | 0.57293 | 757.7029 | 1212.3432
|  |  | 90.8333 | 1007.3667 | 1003.6141 | 650 | 0.096068 | 0.57894 | 758.2818 | 1198.1816
|  |  | 91 | 1007.641 | 1003.898 | 650 | 0.097204 | 0.58486 | 758.8667 | 1184.4729
|  |  | 91.1667 | 1007.9148 | 1004.1814 | 650 | 0.098329 | 0.59067 | 759.4574 | 1171.1997
|  |  | 91.3333 | 1008.1881 | 1004.4642 | 650 | 0.099443 | 0.59639 | 760.0538 | 1158.3456
|  |  | 91.5 | 1008.4609 | 1004.7465 | 650 | 0.10055 | 0.60201 | 760.6558 | 1145.8947
|  |  | 91.6667 | 1008.7332 | 1005.0282 | 650 | 0.10164 | 0.60753 | 761.2633 | 1133.8318
|  |  | 91.8333 | 1009.005 | 1005.3094 | 650 | 0.10272 | 0.61295 | 761.8763 | 1122.1424
|  |  | 92 | 1009.2763 | 1005.5901 | 650 | 0.10379 | 0.61827 | 762.4945 | 1110.8126
|  |  | 92.1667 | 1009.5471 | 1005.8702 | 650 | 0.10485 | 0.62348 | 763.118 | 1099.8288
|  |  | 92.3333 | 1009.8174 | 1006.1498 | 650 | 0.1059 | 0.6286 | 763.7466 | 1089.1784
|  |  | 92.5 | 1010.0873 | 1006.4289 | 650 | 0.10693 | 0.63361 | 764.3802 | 1078.849
|  |  | 92.6667 | 1010.3566 | 1006.7074 | 650 | 0.10796 | 0.63852 | 765.0187 | 1068.8289
|  |  | 92.8333 | 1010.6255 | 1006.9855 | 650 | 0.10897 | 0.64333 | 765.6621 | 1059.1066
|  |  | 93 | 1010.8939 | 1007.263 | 650 | 0.10997 | 0.64803 | 766.3101 | 1049.6714
|  |  | 93.1667 | 1011.1618 | 1007.5399 | 650 | 0.11096 | 0.65264 | 766.9627 | 1040.5128
|  |  | 93.3333 | 1011.4293 | 1007.8164 | 650 | 0.11193 | 0.65714 | 767.6199 | 1031.6208
|  |  | 93.5 | 1011.6962 | 1008.0923 | 650 | 0.1129 | 0.66154 | 768.2814 | 1022.986
|  |  | 93.6667 | 1011.9627 | 1008.3678 | 650 | 0.11385 | 0.66584 | 768.9473 | 1014.599
|  |  | 93.8333 | 1012.2287 | 1008.6427 | 650 | 0.11479 | 0.67004 | 769.6173 | 1006.4511
|  |  | 94 | 1012.4943 | 1008.9171 | 650 | 0.11572 | 0.67414 | 770.2914 | 998.5338
|  |  | 94.1667 | 1012.7593 | 1009.191 | 650 | 0.11664 | 0.67814 | 770.9696 | 990.839
|  |  | 94.3333 | 1013.0239 | 1009.4644 | 650 | 0.11754 | 0.68204 | 771.6516 | 983.3588
|  |  | 94.5 | 1013.2881 | 1009.7373 | 650 | 0.11844 | 0.68585 | 772.3375 | 976.0858
|  |  | 94.6667 | 1013.5518 | 1010.0097 | 650 | 0.11932 | 0.68955 | 773.027 | 969.0129
|  |  | 94.8333 | 1013.815 | 1010.2815 | 650 | 0.12019 | 0.69316 | 773.7202 | 962.133
|  |  | 95 | 1014.0777 | 1010.5529 | 650 | 0.12105 | 0.69668 | 774.4169 | 955.4395
|  |  | 95.1667 | 1014.34 | 1010.8238 | 650 | 0.1219 | 0.7001 | 775.117 | 948.9262
|  |  | 95.3333 | 1014.6018 | 1011.0942 | 650 | 0.12274 | 0.70343 | 775.8204 | 942.5868
|  |  | 95.5 | 1014.8632 | 1011.3641 | 650 | 0.12356 | 0.70666 | 776.5271 | 936.4156
|  |  | 95.6667 | 1015.1241 | 1011.6335 | 650 | 0.12438 | 0.70981 | 777.2369 | 930.4067
|  |  | 95.8333 | 1015.3846 | 1011.9024 | 650 | 0.12518 | 0.71286 | 777.9497 | 924.5549
|  |  | 96 | 1015.6446 | 1012.1708 | 650 | 0.12597 | 0.71583 | 778.6656 | 918.8548
|  |  | 96.1667 | 1015.9041 | 1012.4388 | 650 | 0.12675 | 0.7187 | 779.3843 | 913.3016
|  |  | 96.3333 | 1016.1633 | 1012.7062 | 650 | 0.12752 | 0.72149 | 780.1058 | 907.8902
|  |  | 96.5 | 1016.4219 | 1012.9732 | 650 | 0.12828 | 0.7242 | 780.83 | 902.6162
|  |  | 96.6667 | 1016.6801 | 1013.2397 | 650 | 0.12903 | 0.72682 | 781.5568 | 897.475
|  |  | 96.8333 | 1016.9379 | 1013.5057 | 650 | 0.12977 | 0.72935 | 782.2861 | 892.4624
|  |  | 97 | 1017.1953 | 1013.7712 | 650 | 0.1305 | 0.73181 | 783.0179 | 887.5742
|  |  | 97.1667 | 1017.4521 | 1014.0363 | 650 | 0.13122 | 0.73418 | 783.7521 | 882.8064
|  |  | 97.3333 | 1017.7086 | 1014.3009 | 650 | 0.13193 | 0.73647 | 784.4886 | 878.1552
|  |  | 97.5 | 1017.9646 | 1014.565 | 650 | 0.13263 | 0.73868 | 785.2273 | 873.617
|  |  | 97.6667 | 1018.2202 | 1014.8286 | 650 | 0.13332 | 0.74082 | 785.9681 | 869.1881
|  |  | 97.8333 | 1018.4753 | 1015.0918 | 650 | 0.134 | 0.74288 | 786.711 | 864.8652
|  |  | 98 | 1018.73 | 1015.3545 | 650 | 0.13467 | 0.74486 | 787.4558 | 860.645
|  |  | 98.1667 | 1018.9843 | 1015.6167 | 650 | 0.13533 | 0.74677 | 788.2026 | 856.5243
|  |  | 98.3333 | 1019.2382 | 1015.8785 | 650 | 0.13598 | 0.74861 | 788.9512 | 852.5001
|  |  | 98.5 | 1019.4916 | 1016.1398 | 650 | 0.13662 | 0.75038 | 789.7016 | 848.5693
|  |  | 98.6667 | 1019.7446 | 1016.4007 | 650 | 0.13725 | 0.75207 | 790.4537 | 844.7293
|  |  | 98.8333 | 1019.9971 | 1016.6611 | 650 | 0.13788 | 0.7537 | 791.2074 | 840.9771
|  |  | 99 | 1020.2492 | 1016.921 | 650 | 0.13849 | 0.75526 | 791.9626 | 837.3103
|  |  | 99.1667 | 1020.501 | 1017.1805 | 650 | 0.1391 | 0.75675 | 792.7194 | 833.7263
|  |  | 99.3333 | 1020.7523 | 1017.4395 | 650 | 0.1397 | 0.75817 | 793.4775 | 830.2226
|  |  | 99.5 | 1021.0031 | 1017.6981 | 650 | 0.14028 | 0.75953 | 794.2371 | 826.7968
|  |  | 99.6667 | 1021.2536 | 1017.9562 | 650 | 0.14087 | 0.76083 | 794.9979 | 823.4467
|  |  | 99.8333 | 1021.5036 | 1018.2139 | 650 | 0.14144 | 0.76206 | 795.76 | 820.1701
|  |  | 100 | 1021.7532 | 1018.4711 | 650 | 0.142 | 0.76324 | 796.5232 | 816.9648
|  |  | 100.25 | 1022.1269 | 1018.8699 | 650 | 0.14256 | 1.1472 | 797.6704 | 812.2852
|  |  | 100.5 | 1022.4996 | 1019.2662 | 650 | 0.14338 | 1.1495 | 798.8199 | 807.7549
|  |  | 100.75 | 1022.8714 | 1019.6601 | 650 | 0.14419 | 1.1517 | 799.9715 | 803.3676
|  |  | 101 | 1023.2422 | 1020.0518 | 650 | 0.14497 | 1.1536 | 801.1251 | 799.1172
|  |  | 101.25 | 1023.6122 | 1020.4414 | 650 | 0.14575 | 1.1554 | 802.2805 | 794.9982
|  |  | 101.5 | 1023.9812 | 1020.8291 | 650 | 0.1465 | 1.157 | 803.4375 | 791.0052
|  |  | 101.75 | 1024.3494 | 1021.215 | 650 | 0.14724 | 1.1584 | 804.5959 | 787.1331
|  |  | 102 | 1024.7166 | 1021.5991 | 650 | 0.14796 | 1.1597 | 805.7555 | 783.377
|  |  | 102.25 | 1025.0829 | 1021.9816 | 650 | 0.14867 | 1.1608 | 806.9163 | 779.7322
|  |  | 102.5 | 1025.4484 | 1022.3625 | 650 | 0.14937 | 1.1617 | 808.078 | 776.1944
|  |  | 102.75 | 1025.8129 | 1022.7419 | 650 | 0.15005 | 1.1625 | 809.2404 | 772.7595
|  |  | 103 | 1026.1766 | 1023.1199 | 650 | 0.15072 | 1.1631 | 810.4035 | 769.4233
|  |  | 103.25 | 1026.5394 | 1023.4965 | 650 | 0.15137 | 1.1636 | 811.5671 | 766.1821
|  |  | 103.5 | 1026.9013 | 1023.8717 | 650 | 0.15201 | 1.1639 | 812.731 | 763.0323
|  |  | 103.75 | 1027.2624 | 1024.2457 | 650 | 0.15264 | 1.1641 | 813.8951 | 759.9704
|  |  | 104 | 1027.6225 | 1024.6185 | 650 | 0.15325 | 1.1642 | 815.0593 | 756.9931
|  |  | 104.25 | 1027.9818 | 1024.99 | 650 | 0.15386 | 1.1641 | 816.2235 | 754.0973
|  |  | 104.5 | 1028.3403 | 1025.3604 | 650 | 0.15445 | 1.164 | 817.3875 | 751.2799
|  |  | 104.75 | 1028.6979 | 1025.7297 | 650 | 0.15503 | 1.1637 | 818.5511 | 748.5382
|  |  | 105 | 1029.0546 | 1026.0978 | 650 | 0.15559 | 1.1633 | 819.7144 | 745.8694
|  |  | 105.25 | 1029.4105 | 1026.4649 | 650 | 0.15615 | 1.1627 | 820.8771 | 743.2708
|  |  | 105.5 | 1029.7656 | 1026.8309 | 650 | 0.1567 | 1.1621 | 822.0392 | 740.7399
|  |  | 105.75 | 1030.1198 | 1027.1959 | 650 | 0.15723 | 1.1613 | 823.2005 | 738.2744
|  |  | 106 | 1030.4732 | 1027.5598 | 650 | 0.15776 | 1.1605 | 824.361 | 735.872
|  |  | 106.25 | 1030.8257 | 1027.9228 | 650 | 0.15827 | 1.1595 | 825.5205 | 733.5304
|  |  | 106.5 | 1031.1774 | 1028.2848 | 650 | 0.15878 | 1.1585 | 826.679 | 731.2477
|  |  | 106.75 | 1031.5283 | 1028.6458 | 650 | 0.15927 | 1.1574 | 827.8364 | 729.0217
|  |  | 107 | 1031.8784 | 1029.0059 | 650 | 0.15976 | 1.1561 | 828.9925 | 726.8506
|  |  | 107.25 | 1032.2276 | 1029.3651 | 650 | 0.16024 | 1.1548 | 830.1473 | 724.7325
|  |  | 107.5 | 1032.5761 | 1029.7233 | 650 | 0.1607 | 1.1534 | 831.3007 | 722.6657
|  |  | 107.75 | 1032.9237 | 1030.0806 | 650 | 0.16116 | 1.1519 | 832.4527 | 720.6484
|  |  | 108 | 1033.2706 | 1030.437 | 650 | 0.16162 | 1.1504 | 833.603 | 718.6791
|  |  | 108.25 | 1033.6166 | 1030.7924 | 650 | 0.16206 | 1.1487 | 834.7517 | 716.7562
|  |  | 108.5 | 1033.9618 | 1031.1471 | 650 | 0.16249 | 1.147 | 835.8987 | 714.8781
|  |  | 108.75 | 1034.3063 | 1031.5008 | 650 | 0.16292 | 1.1452 | 837.044 | 713.0435
|  |  | 109 | 1034.6499 | 1031.8536 | 650 | 0.16334 | 1.1434 | 838.1873 | 711.251
|  |  | 109.25 | 1034.9928 | 1032.2056 | 650 | 0.16375 | 1.1414 | 839.3288 | 709.4992
|  |  | 109.5 | 1035.3349 | 1032.5568 | 650 | 0.16415 | 1.1395 | 840.4683 | 707.7869
|  |  | 109.75 | 1035.6762 | 1032.907 | 650 | 0.16455 | 1.1374 | 841.6057 | 706.1129
|  |  | 110 | 1036.0167 | 1033.2565 | 650 | 0.16494 | 1.1353 | 842.741 | 704.476
|  |  | 110.25 | 1036.3564 | 1033.6051 | 650 | 0.16533 | 1.1331 | 843.8741 | 702.875
|  |  | 110.5 | 1036.6954 | 1033.9529 | 650 | 0.1657 | 1.1309 | 845.005 | 701.3089
|  |  | 110.75 | 1037.0336 | 1034.2998 | 650 | 0.16607 | 1.1286 | 846.1337 | 699.7766
|  |  | 111 | 1037.3711 | 1034.6459 | 650 | 0.16644 | 1.1263 | 847.26 | 698.2772
|  |  | 111.25 | 1037.7078 | 1034.9912 | 650 | 0.16679 | 1.1239 | 848.3839 | 696.8096
|  |  | 111.5 | 1038.0438 | 1035.3357 | 650 | 0.16714 | 1.1215 | 849.5054 | 695.3729
|  |  | 111.75 | 1038.3789 | 1035.6794 | 650 | 0.16749 | 1.119 | 850.6244 | 693.9662
|  |  | 112 | 1038.7134 | 1036.0223 | 650 | 0.16783 | 1.1165 | 851.7409 | 692.5887
|  |  | 112.25 | 1039.0471 | 1036.3644 | 650 | 0.16816 | 1.1139 | 852.8549 | 691.2396
|  |  | 112.5 | 1039.3801 | 1036.7057 | 650 | 0.16849 | 1.1113 | 853.9662 | 689.9179
|  |  | 112.75 | 1039.7123 | 1037.0462 | 650 | 0.16881 | 1.1087 | 855.0749 | 688.623
|  |  | 113 | 1040.0438 | 1037.3859 | 650 | 0.16913 | 1.106 | 856.1809 | 687.354
|  |  | 113.25 | 1040.3745 | 1037.7249 | 650 | 0.16944 | 1.1033 | 857.2842 | 686.1103
|  |  | 113.5 | 1040.7045 | 1038.0631 | 650 | 0.16975 | 1.1005 | 858.3847 | 684.8912
|  |  | 113.75 | 1041.0338 | 1038.4005 | 650 | 0.17005 | 1.0977 | 859.4824 | 683.696
|  |  | 114 | 1041.3624 | 1038.7371 | 650 | 0.17035 | 1.0949 | 860.5773 | 682.5241
|  |  | 114.25 | 1041.6903 | 1039.0729 | 650 | 0.17064 | 1.092 | 861.6693 | 681.3748
|  |  | 114.5 | 1042.0174 | 1039.4081 | 650 | 0.17093 | 1.0892 | 862.7585 | 680.2475
|  |  | 114.75 | 1042.3439 | 1039.7424 | 650 | 0.17121 | 1.0862 | 863.8447 | 679.1416
|  |  | 115 | 1042.6696 | 1040.076 | 650 | 0.17149 | 1.0833 | 864.928 | 678.0566
|  |  | 115.25 | 1042.9946 | 1040.4088 | 650 | 0.17177 | 1.0803 | 866.0083 | 676.9919
|  |  | 115.5 | 1043.3189 | 1040.7409 | 650 | 0.17204 | 1.0773 | 867.0856 | 675.947
|  |  | 115.75 | 1043.6425 | 1041.0723 | 650 | 0.1723 | 1.0743 | 868.1599 | 674.9213
|  |  | 116 | 1043.9654 | 1041.4029 | 650 | 0.17256 | 1.0712 | 869.2312 | 673.9145
|  |  | 116.25 | 1044.2876 | 1041.7328 | 650 | 0.17282 | 1.0682 | 870.2993 | 672.9259
|  |  | 116.5 | 1044.6092 | 1042.0619 | 650 | 0.17308 | 1.0651 | 871.3644 | 671.9552
|  |  | 116.75 | 1044.93 | 1042.3904 | 650 | 0.17333 | 1.062 | 872.4264 | 671.0019
|  |  | 117 | 1045.2502 | 1042.718 | 650 | 0.17357 | 1.0588 | 873.4852 | 670.0656
|  |  | 117.25 | 1045.5696 | 1043.045 | 650 | 0.17382 | 1.0557 | 874.5409 | 669.1458
|  |  | 117.5 | 1045.8884 | 1043.3713 | 650 | 0.17405 | 1.0525 | 875.5935 | 668.2421
|  |  | 117.75 | 1046.2065 | 1043.6968 | 650 | 0.17429 | 1.0493 | 876.6428 | 667.3541
|  |  | 118 | 1046.524 | 1044.0216 | 650 | 0.17452 | 1.0461 | 877.6889 | 666.4816
|  |  | 118.25 | 1046.8407 | 1044.3457 | 650 | 0.17475 | 1.0429 | 878.7319 | 665.6239
|  |  | 118.5 | 1047.1568 | 1044.6691 | 650 | 0.17498 | 1.0397 | 879.7715 | 664.781
|  |  | 118.75 | 1047.4723 | 1044.9918 | 650 | 0.1752 | 1.0365 | 880.808 | 663.9523
|  |  | 119 | 1047.7871 | 1045.3139 | 650 | 0.17542 | 1.0332 | 881.8412 | 663.1375
|  |  | 119.25 | 1048.1012 | 1045.6352 | 650 | 0.17563 | 1.0299 | 882.8711 | 662.3363
|  |  | 119.5 | 1048.4146 | 1045.9558 | 650 | 0.17584 | 1.0266 | 883.8978 | 661.5485
|  |  | 119.75 | 1048.7274 | 1046.2757 | 650 | 0.17605 | 1.0234 | 884.9211 | 660.7736
|  |  | 120 | 1049.0396 | 1046.5949 | 650 | 0.17626 | 1.0201 | 885.9412 | 660.0114
|  |  | 120.25 | 1049.3511 | 1046.9135 | 650 | 0.17646 | 1.0167 | 886.9579 | 659.2616
|  |  | 120.5 | 1049.6619 | 1047.2313 | 650 | 0.17666 | 1.0134 | 887.9714 | 658.5239
|  |  | 120.75 | 1049.9721 | 1047.5485 | 650 | 0.17686 | 1.0101 | 888.9815 | 657.798
|  |  | 121 | 1050.2817 | 1047.865 | 650 | 0.17706 | 1.0068 | 889.9882 | 657.0838
|  |  | 121.25 | 1050.5906 | 1048.1809 | 650 | 0.17725 | 1.0034 | 890.9917 | 656.3808
|  |  | 121.5 | 1050.8989 | 1048.496 | 650 | 0.17744 | 1.0001 | 891.9918 | 655.6889
|  |  | 121.75 | 1051.2066 | 1048.8105 | 650 | 0.17763 | 0.99673 | 892.9885 | 655.0078
|  |  | 122 | 1051.5136 | 1049.1244 | 650 | 0.17781 | 0.99338 | 893.9819 | 654.3373
|  |  | 122.25 | 1051.82 | 1049.4375 | 650 | 0.17799 | 0.99002 | 894.9719 | 653.6772
|  |  | 122.5 | 1052.1258 | 1049.7501 | 650 | 0.17817 | 0.98665 | 895.9585 | 653.0271
|  |  | 122.75 | 1052.431 | 1050.0619 | 650 | 0.17835 | 0.98328 | 896.9418 | 652.387
|  |  | 123 | 1052.7355 | 1050.3731 | 650 | 0.17853 | 0.97991 | 897.9217 | 651.7566
|  |  | 123.25 | 1053.0394 | 1050.6837 | 650 | 0.1787 | 0.97654 | 898.8983 | 651.1357
|  |  | 123.5 | 1053.3427 | 1050.9936 | 650 | 0.17887 | 0.97316 | 899.8714 | 650.5241
|  |  | 123.75 | 1053.6454 | 1051.3028 | 650 | 0.17904 | 0.96978 | 900.8412 | 650
|  |  | 124 | 1053.9475 | 1051.6115 | 650 | 0.17918 | 0.96629 | 901.8075 | 650
|  |  | 124.25 | 1054.249 | 1051.9194 | 650 | 0.17918 | 0.96209 | 902.7696 | 650
|  |  | 124.5 | 1054.5498 | 1052.2268 | 650 | 0.17918 | 0.9579 | 903.7275 | 650
|  |  | 124.75 | 1054.8501 | 1052.5335 | 650 | 0.17918 | 0.95374 | 904.6812 | 650
|  |  | 125 | 1055.1498 | 1052.8396 | 650 | 0.17918 | 0.9496 | 905.6308 | 650
|  |  | 125.25 | 1055.4488 | 1053.145 | 650 | 0.17918 | 0.94548 | 906.5763 | 650
|  |  | 125.5 | 1055.7473 | 1053.4498 | 650 | 0.17918 | 0.94138 | 907.5177 | 650
|  |  | 125.75 | 1056.0452 | 1053.754 | 650 | 0.17918 | 0.93731 | 908.455 | 650
|  |  | 126 | 1056.3425 | 1054.0576 | 650 | 0.17918 | 0.93326 | 909.3882 | 650
|  |  | 126.25 | 1056.6391 | 1054.3606 | 650 | 0.17918 | 0.92923 | 910.3175 | 650
|  |  | 126.5 | 1056.9353 | 1054.6629 | 650 | 0.17918 | 0.92522 | 911.2427 | 650
|  |  | 126.75 | 1057.2308 | 1054.9646 | 650 | 0.17918 | 0.92123 | 912.1639 | 650
|  |  | 127 | 1057.5257 | 1055.2657 | 650 | 0.17918 | 0.91727 | 913.0812 | 650
|  |  | 127.25 | 1057.8201 | 1055.5662 | 650 | 0.17918 | 0.91333 | 913.9945 | 650
|  |  | 127.5 | 1058.1139 | 1055.8661 | 650 | 0.17918 | 0.9094 | 914.9039 | 650
|  |  | 127.75 | 1058.4071 | 1056.1654 | 650 | 0.17918 | 0.9055 | 915.8094 | 650
|  |  | 128 | 1058.6997 | 1056.4641 | 650 | 0.17918 | 0.90162 | 916.7111 | 650
|  |  | 128.25 | 1058.9918 | 1056.7622 | 650 | 0.17918 | 0.89777 | 917.6088 | 650
|  |  | 128.5 | 1059.2833 | 1057.0597 | 650 | 0.17918 | 0.89393 | 918.5028 | 650
|  |  | 128.75 | 1059.5742 | 1057.3566 | 650 | 0.17918 | 0.89011 | 919.3929 | 650
|  |  | 129 | 1059.8646 | 1057.6529 | 650 | 0.17918 | 0.88631 | 920.2792 | 650
|  |  | 129.25 | 1060.1544 | 1057.9486 | 650 | 0.17918 | 0.88254 | 921.1617 | 650
|  |  | 129.5 | 1060.4437 | 1058.2438 | 650 | 0.17918 | 0.87878 | 922.0405 | 650
|  |  | 129.75 | 1060.7324 | 1058.5383 | 650 | 0.17918 | 0.87505 | 922.9155 | 650
|  |  | 130 | 1061.0205 | 1058.8323 | 650 | 0.17918 | 0.87133 | 923.7869 | 650
|  |  | 130.25 | 1061.3081 | 1059.1257 | 650 | 0.17918 | 0.86764 | 924.6545 | 650
|  |  | 130.5 | 1061.5951 | 1059.4185 | 650 | 0.17918 | 0.86396 | 925.5185 | 650
|  |  | 130.75 | 1061.8816 | 1059.7107 | 650 | 0.17918 | 0.86031 | 926.3788 | 650
|  |  | 131 | 1062.1675 | 1060.0024 | 650 | 0.17918 | 0.85667 | 927.2355 | 650
|  |  | 131.25 | 1062.4529 | 1060.2935 | 650 | 0.17918 | 0.85306 | 928.0885 | 650
|  |  | 131.5 | 1062.7378 | 1060.584 | 650 | 0.17918 | 0.84946 | 928.938 | 650
|  |  | 131.75 | 1063.0221 | 1060.8739 | 650 | 0.17918 | 0.84588 | 929.7839 | 650
|  |  | 132 | 1063.3059 | 1061.1633 | 650 | 0.17918 | 0.84232 | 930.6262 | 650
|  |  | 132.25 | 1063.5891 | 1061.4522 | 650 | 0.17918 | 0.83879 | 931.465 | 650
|  |  | 132.5 | 1063.8718 | 1061.7404 | 650 | 0.17918 | 0.83527 | 932.3002 | 650
|  |  | 132.75 | 1064.154 | 1062.0281 | 650 | 0.17918 | 0.83177 | 933.132 | 650
|  |  | 133 | 1064.4356 | 1062.3153 | 650 | 0.17918 | 0.82828 | 933.9603 | 650
|  |  | 133.25 | 1064.7167 | 1062.6019 | 650 | 0.17918 | 0.82482 | 934.7851 | 650
|  |  | 133.5 | 1064.9973 | 1062.8879 | 650 | 0.17918 | 0.82138 | 935.6065 | 650
|  |  | 133.75 | 1065.2774 | 1063.1734 | 650 | 0.17918 | 0.81795 | 936.4244 | 650
|  |  | 134 | 1065.5569 | 1063.4584 | 650 | 0.17918 | 0.81454 | 937.239 | 650
|  |  | 134.25 | 1065.8359 | 1063.7428 | 650 | 0.17918 | 0.81115 | 938.0501 | 650
|  |  | 134.5 | 1066.1144 | 1064.0267 | 650 | 0.17918 | 0.80778 | 938.8579 | 650
|  |  | 134.75 | 1066.3924 | 1064.31 | 650 | 0.17918 | 0.80443 | 939.6623 | 650
|  |  | 135 | 1066.6699 | 1064.5928 | 650 | 0.17918 | 0.80109 | 940.4634 | 650
|  |  | 135.25 | 1066.9468 | 1064.875 | 650 | 0.17918 | 0.79777 | 941.2612 | 650
|  |  | 135.5 | 1067.2233 | 1065.1567 | 650 | 0.17918 | 0.79447 | 942.0557 | 650
|  |  | 135.75 | 1067.4992 | 1065.4379 | 650 | 0.17918 | 0.79119 | 942.8469 | 650
|  |  | 136 | 1067.7746 | 1065.7186 | 650 | 0.17918 | 0.78793 | 943.6348 | 650
|  |  | 136.25 | 1068.0495 | 1065.9987 | 650 | 0.17918 | 0.78468 | 944.4195 | 650
|  |  | 136.5 | 1068.324 | 1066.2783 | 650 | 0.17918 | 0.78145 | 945.2009 | 650
|  |  | 136.75 | 1068.5979 | 1066.5573 | 650 | 0.17918 | 0.77824 | 945.9792 | 650
|  |  | 137 | 1068.8713 | 1066.8359 | 650 | 0.17918 | 0.77504 | 946.7542 | 650
|  |  | 137.25 | 1069.1442 | 1067.1139 | 650 | 0.17918 | 0.77187 | 947.5261 | 650
|  |  | 137.5 | 1069.4166 | 1067.3914 | 650 | 0.17918 | 0.76871 | 948.2948 | 650
|  |  | 137.75 | 1069.6886 | 1067.6684 | 650 | 0.17918 | 0.76556 | 949.0604 | 650
|  |  | 138 | 1069.96 | 1067.9449 | 650 | 0.17918 | 0.76243 | 949.8228 | 650
|  |  | 138.25 | 1070.2309 | 1068.2209 | 650 | 0.17918 | 0.75932 | 950.5821 | 650
|  |  | 138.5 | 1070.5014 | 1068.4963 | 650 | 0.17918 | 0.75623 | 951.3383 | 650
|  |  | 138.75 | 1070.7714 | 1068.7713 | 650 | 0.17918 | 0.75315 | 952.0915 | 650
|  |  | 139 | 1071.0408 | 1069.0457 | 650 | 0.17918 | 0.75009 | 952.8416 | 650
|  |  | 139.25 | 1071.3098 | 1069.3196 | 650 | 0.17918 | 0.74705 | 953.5886 | 650
|  |  | 139.5 | 1071.5783 | 1069.593 | 650 | 0.17918 | 0.74402 | 954.3326 | 650
|  |  | 139.75 | 1071.8464 | 1069.866 | 650 | 0.17918 | 0.74101 | 955.0737 | 650
|  |  | 140 | 1072.1139 | 1070.1384 | 650 | 0.17918 | 0.73801 | 955.8117 | 650
|  |  | 140.25 | 1072.381 | 1070.4103 | 650 | 0.17918 | 0.73503 | 956.5467 | 650
|  |  | 140.5 | 1072.6476 | 1070.6818 | 650 | 0.17918 | 0.73206 | 957.2788 | 650
|  |  | 140.75 | 1072.9138 | 1070.9527 | 650 | 0.17918 | 0.72912 | 958.0079 | 650
|  |  | 141 | 1073.1794 | 1071.2231 | 650 | 0.17918 | 0.72618 | 958.7341 | 650
|  |  | 141.25 | 1073.4446 | 1071.4931 | 650 | 0.17918 | 0.72327 | 959.4573 | 650
|  |  | 141.5 | 1073.7093 | 1071.7626 | 650 | 0.17918 | 0.72036 | 960.1777 | 650
|  |  | 141.75 | 1073.9736 | 1072.0315 | 650 | 0.17918 | 0.71748 | 960.8952 | 650
|  |  | 142 | 1074.2374 | 1072.3 | 650 | 0.17918 | 0.71461 | 961.6098 | 650
|  |  | 142.25 | 1074.5007 | 1072.568 | 650 | 0.17918 | 0.71175 | 962.3215 | 650
|  |  | 142.5 | 1074.7635 | 1072.8356 | 650 | 0.17918 | 0.70891 | 963.0304 | 650
|  |  | 142.75 | 1075.0259 | 1073.1026 | 650 | 0.17918 | 0.70608 | 963.7365 | 650
|  |  | 143 | 1075.2879 | 1073.3692 | 650 | 0.17918 | 0.70327 | 964.4398 | 650
|  |  | 143.25 | 1075.5494 | 1073.6353 | 650 | 0.17918 | 0.70048 | 965.1403 | 650
|  |  | 143.5 | 1075.8104 | 1073.9009 | 650 | 0.17918 | 0.6977 | 965.838 | 650
|  |  | 143.75 | 1076.071 | 1074.1661 | 650 | 0.17918 | 0.69493 | 966.5329 | 650
|  |  | 144 | 1076.3311 | 1074.4307 | 650 | 0.17918 | 0.69218 | 967.2251 | 650
|  |  | 144.25 | 1076.5908 | 1074.6949 | 650 | 0.17918 | 0.68944 | 967.9145 | 650
|  |  | 144.5 | 1076.85 | 1074.9587 | 650 | 0.17918 | 0.68672 | 968.6012 | 650
|  |  | 144.75 | 1077.1088 | 1075.2219 | 650 | 0.17918 | 0.68401 | 969.2852 | 650
|  |  | 145 | 1077.3671 | 1075.4847 | 650 | 0.17918 | 0.68132 | 969.9666 | 650
|  |  | 145.25 | 1077.625 | 1075.7471 | 650 | 0.17918 | 0.67864 | 970.6452 | 650
|  |  | 145.5 | 1077.8824 | 1076.009 | 650 | 0.17918 | 0.67597 | 971.3212 | 650
|  |  | 145.75 | 1078.1394 | 1076.2704 | 650 | 0.17918 | 0.67332 | 971.9945 | 650
|  |  | 146 | 1078.396 | 1076.5313 | 650 | 0.17918 | 0.67068 | 972.6652 | 650
|  |  | 146.25 | 1078.6521 | 1076.7918 | 650 | 0.17918 | 0.66806 | 973.3332 | 650
|  |  | 146.5 | 1078.9078 | 1077.0519 | 650 | 0.17918 | 0.66545 | 973.9987 | 650
|  |  | 146.75 | 1079.1631 | 1077.3115 | 650 | 0.17918 | 0.66286 | 974.6615 | 650
|  |  | 147 | 1079.4179 | 1077.5706 | 650 | 0.17918 | 0.66027 | 975.3218 | 650
|  |  | 147.25 | 1079.6723 | 1077.8293 | 650 | 0.17918 | 0.65771 | 975.9795 | 650
|  |  | 147.5 | 1079.9262 | 1078.0876 | 650 | 0.17918 | 0.65515 | 976.6347 | 650
|  |  | 147.75 | 1080.1797 | 1078.3454 | 650 | 0.17918 | 0.65261 | 977.2873 | 650
|  |  | 148 | 1080.4328 | 1078.6027 | 650 | 0.17918 | 0.65008 | 977.9374 | 650
|  |  | 148.25 | 1080.6855 | 1078.8596 | 650 | 0.17918 | 0.64757 | 978.5849 | 650
|  |  | 148.5 | 1080.9377 | 1079.1161 | 650 | 0.17918 | 0.64507 | 979.23 | 650
|  |  | 148.75 | 1081.1896 | 1079.3721 | 650 | 0.17918 | 0.64258 | 979.8726 | 650
|  |  | 149 | 1081.441 | 1079.6277 | 650 | 0.17918 | 0.6401 | 980.5127 | 650
|  |  | 149.25 | 1081.6919 | 1079.8828 | 650 | 0.17918 | 0.63764 | 981.1503 | 650
|  |  | 149.5 | 1081.9425 | 1080.1376 | 650 | 0.17918 | 0.63519 | 981.7855 | 650
|  |  | 149.75 | 1082.1926 | 1080.3918 | 650 | 0.17918 | 0.63275 | 982.4183 | 650
|  |  | 150 | 1082.4423 | 1080.6457 | 650 | 0.17918 | 0.63033 | 983.0486 | 650